## Signal Strength
Signal(function code 04 read)
No. | address Decimal | address Hexadecimal | Name | Data Type | Default | Range | Unit | Mark
1 | 4870 | 1306 | Signal strength | Unsigned 16 bit | 0 | 0～99 | ——
2 | 4871 | 1307 | Network statue | Unsigned 16 bit |  | 0~100 | ——

## 0XXX
Basic Parameters (function code 04 read)
No. | address Decimal | Address Hexadecimal | Name | Default | Range（Big Endian）
1 | 0 | 0000 | connected total Sensor QTY | 0 | 0～64
2 | 1 | 0001 | Connecttting Sensor | 0 | 0～64
3 | 2 | 0002 | Disconnected Sensor | 0 | 0～64
4 | 3 | 0003 | Sensor No. 1 connection statue |  | 0～3600(second)
5 | 4 | 0004 | connect Sensor 1 address low bit |  | 0～65535
6 | 5 | 0005 | connect Sensor 1 address high bit |  | 0～65535
7 | 6 | 0006 | high byte: sensor wireless signal strength low byte: Sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
8 | 7 | 0007 | Sensor 1 current |  | 0～65535(*0.1)
9 | 8 | 0008 | Sensor 1 temperature |  | 0～65535(*0.1)
10 | 9 | 0009 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
11 | 10 | 000A | current sensor count digit |  | 0～65535
12 | 11 | 000B | reserved
13 | 12 | 000C | Sensor 2 connection statue |  | 0～3600(second)
14 | 13 | 000D | connect sensor No. 2 address low bit |  | 0～65535
15 | 14 | 000E | connect sensor No. 2 address high bit |  | 0～65535
16 | 15 | 000F | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
17 | 16 | 0010 | Sensor 2 current |  | 0～65535(*0.1)
18 | 17 | 0011 | Sensor 2 temperature |  | 0～65535(*0.1)
19 | 18 | 0012 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
20 | 19 | 0013 | current sensor count digit |  | 0～65535
21 | 20 | 0014 | reserved
22 | 21 | 0015 | Sensor 3 connection statue |  | 0～3600(second)
23 | 22 | 0016 | connect sensor No. 3 address low bit |  | 0～65535
24 | 23 | 0017 | connect sensor No. 3 address high bit |  | 0～65535
25 | 24 | 0018 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
26 | 25 | 0019 | Sensor 3 current |  | 0～65535(*0.1)
27 | 26 | 001A | Sensor 3 temperature |  | 0～65535(*0.1)
28 | 27 | 001B | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
29 | 28 | 001C | current sensor count digit |  | 0～65535
30 | 29 | 001D | reserved
31 | 30 | 001E | Sensor 4 connection statue |  | 0～3600(second)
32 | 31 | 001F | connect sensor No. 4 address low bit |  | 0～65535
33 | 32 | 0020 | connect sensor No. 4 address high bit |  | 0～65535
34 | 33 | 0021 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
35 | 34 | 0022 | Sensor 4 current |  | 0～65535(*0.1)
36 | 35 | 0023 | Sensor 4 temperature |  | 0～65535(*0.1)
37 | 36 | 0024 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
38 | 37 | 0025 | current sensor count digit |  | 0～65535
39 | 38 | 0026 | reserved
40 | 39 | 0027 | Sensor 5 connection statue |  | 0～3600(second)
41 | 40 | 0028 | connect sensor No. 5 address low bit |  | 0～65535
42 | 41 | 0029 | connect sensor No. 5 address high bit |  | 0～65535
43 | 42 | 002A | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
44 | 43 | 002B | Sensor 5 current |  | 0～65535(*0.1)
45 | 44 | 002C | Sensor 5 temperature |  | 0～65535(*0.1)
46 | 45 | 002D | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
47 | 46 | 002E | current sensor count digit |  | 0～65535
48 | 47 | 002F | reserved
49 | 48 | 0030 | Sensor 6 connection statue |  | 0～3600(second)
50 | 49 | 0031 | connect sensor No. 6 address low bit |  | 0～65535
51 | 50 | 0032 | connect sensor No. 6 address high bit |  | 0～65535
52 | 51 | 0033 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
53 | 52 | 0034 | Sensor 6 current |  | 0～65535(*0.1)
54 | 53 | 0035 | Sensor 6 temperature |  | 0～65535(*0.1)
55 | 54 | 0036 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
56 | 55 | 0037 | current sensor count digit |  | 0～65535
57 | 56 | 0038 | reserved
58 | 57 | 0039 | Sensor 7 connection statue |  | 0～3600(second)
59 | 58 | 003A | connect sensor No. 7 address low bit |  | 0～65535
60 | 59 | 003B | connect sensor No. 7 address high bit |  | 0～65535
61 | 60 | 003C | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
62 | 61 | 003D | Sensor 7 current |  | 0～65535(*0.1)
63 | 62 | 003E | Sensor 7 temperature |  | 0～65535(*0.1)
64 | 63 | 003F | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
65 | 64 | 0040 | current sensor count digit |  | 0～65535
66 | 65 | 0041 | reserved
67 | 66 | 0042 | Sensor 8 connection statue |  | 0～3600(second)
68 | 67 | 0043 | connect sensor No. 8 address low bit |  | 0～65535
69 | 68 | 0044 | connect sensor No. 8 address high bit |  | 0～65535
70 | 69 | 0045 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
71 | 70 | 0046 | Sensor 8 current |  | 0～65535(*0.1)
72 | 71 | 0047 | Sensor 8 temperature |  | 0～65535(*0.1)
73 | 72 | 0048 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
74 | 73 | 0049 | current sensor count digit |  | 0～65535
75 | 74 | 004A | reserved
76 | 75 | 004B | Sensor 9 connection statue |  | 0～3600(second)
77 | 76 | 004C | connect sensor No. 9 address low bit |  | 0～65535
78 | 77 | 004D | connect sensor No. 9 address high bit |  | 0～65535
79 | 78 | 004E | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
80 | 79 | 004F | Sensor 9 current |  | 0～65535(*0.1)
81 | 80 | 0050 | Sensor 9 temperature |  | 0～65535(*0.1)
82 | 81 | 0051 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
83 | 82 | 0052 | current sensor count digit |  | 0～65535
84 | 83 | 0053 | reserved
85 | 84 | 0054 | Sensor 10 connection statue |  | 0～3600(second)
86 | 85 | 0055 | connect sensor No. 10 address low bit |  | 0～65535
87 | 86 | 0056 | connect sensor No. 10 address high bit |  | 0～65535
88 | 87 | 0057 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
89 | 88 | 0058 | Sensor 10 current |  | 0～65535(*0.1)
90 | 89 | 0059 | Sensor 10 temperature |  | 0～65535(*0.1)
91 | 90 | 005A | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
92 | 91 | 005B | current sensor count digit |  | 0～65535
93 | 92 | 005C | reserved
94 | 93 | 005D | Sensor 11 connection statue |  | 0～3600(second)
95 | 94 | 005E | connect sensor No. 11 address low bit |  | 0～65535
96 | 95 | 005F | connect sensor No. 11 address high bit |  | 0～65535
97 | 96 | 0060 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
98 | 97 | 0061 | Sensor 11 current |  | 0～65535(*0.1)
99 | 98 | 0062 | Sensor 11 temperature |  | 0～65535(*0.1)
100 | 99 | 0063 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
101 | 100 | 0064 | current sensor count digit |  | 0～65535
102 | 101 | 0065 | reserved
103 | 102 | 0066 | Sensor 12 connection statue |  | 0～3600(second)
104 | 103 | 0067 | connect sensor No. 12 address low bit |  | 0～65535
105 | 104 | 0068 | connect sensor No. 12 address high bit |  | 0～65535
106 | 105 | 0069 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
107 | 106 | 006A | Sensor 12 current |  | 0～65535(*0.1)
108 | 107 | 006B | Sensor 12 temperature |  | 0～65535(*0.1)
109 | 108 | 006C | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
110 | 109 | 006D | current sensor count digit |  | 0～65535
111 | 110 | 006E | reserved
112 | 111 | 006F | Sensor 13 connection statue |  | 0～3600(second)
113 | 112 | 0070 | connect sensor No. 13 address low bit |  | 0～65535
114 | 113 | 0071 | connect sensor No. 13 address high bit |  | 0～65535
115 | 114 | 0072 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
116 | 115 | 0073 | Sensor 13 current |  | 0～65535(*0.1)
117 | 116 | 0074 | Sensor 13 temperature |  | 0～65535(*0.1)
118 | 117 | 0075 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
119 | 118 | 0076 | current sensor count digit |  | 0～65535
120 | 119 | 0077 | reserved
121 | 120 | 0078 | Sensor 14 connection statue |  | 0～3600(second)
122 | 121 | 0079 | connect sensor No. 14 address low bit |  | 0～65535
123 | 122 | 007A | connect sensor No. 14 address high bit |  | 0～65535
124 | 123 | 007B | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
125 | 124 | 007C | Sensor 14 current |  | 0～65535(*0.1)
126 | 125 | 007D | Sensor 14 temperature |  | 0～65535(*0.1)
127 | 126 | 007E | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
128 | 127 | 007F | current sensor count digit |  | 0～65535
129 | 128 | 0080 | reserved
130 | 129 | 0081 | Sensor 15 connection statue |  | 0～3600(second)
131 | 130 | 0082 | connect sensor No. 15 address low bit |  | 0～65535
132 | 131 | 0083 | connect sensor No. 15 address high bit |  | 0～65535
133 | 132 | 0084 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
134 | 133 | 0085 | Sensor 15 current |  | 0～65535(*0.1)
135 | 134 | 0086 | Sensor 15 temperature |  | 0～65535(*0.1)
136 | 135 | 0087 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
137 | 136 | 0088 | current sensor count digit |  | 0～65535
138 | 137 | 0089 | reserved
139 | 138 | 008A | Sensor 16 connection statue |  | 0～3600(second)
140 | 139 | 008B | connect sensor No. 16 address low bit |  | 0～65535
141 | 140 | 008C | connect sensor No. 16 address high bit |  | 0～65535
142 | 141 | 008D | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
143 | 142 | 008E | Sensor 16 current |  | 0～65535(*0.1)
144 | 143 | 008F | Sensor 16 temperature |  | 0～65535(*0.1)
145 | 144 | 0090 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
146 | 145 | 0091 | current sensor count digit |  | 0～65535
147 | 146 | 0092 | reserved
148 | 147 | 0093 | Sensor 17 connection statue |  | 0～3600(second)
149 | 148 | 0094 | connect sensor No. 17 address low bit |  | 0～65535
150 | 149 | 0095 | connect sensor No. 17 address high bit |  | 0～65535
151 | 150 | 0096 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
152 | 151 | 0097 | Sensor 17 current |  | 0～65535(*0.1)
153 | 152 | 0098 | Sensor 17 temperature |  | 0～65535(*0.1)
154 | 153 | 0099 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
155 | 154 | 009A | current sensor count digit |  | 0～65535
156 | 155 | 009B | reserved
157 | 156 | 009C | Sensor 18 connection statue |  | 0～3600(second)
158 | 157 | 009D | connect sensor No. 18 address low bit |  | 0～65535
159 | 158 | 009E | connect sensor No. 18 address high bit |  | 0～65535
160 | 159 | 009F | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
161 | 160 | 00A0 | Sensor 18 current |  | 0～65535(*0.1)
162 | 161 | 00A1 | Sensor 18 temperature |  | 0～65535(*0.1)
163 | 162 | 00A2 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
164 | 163 | 00A3 | current sensor count digit |  | 0～65535
165 | 164 | 00A4 | reserved
166 | 165 | 00A5 | Sensor 19 connection statue |  | 0～3600(second)
167 | 166 | 00A6 | connect sensor No. 19 address low bit |  | 0～65535
168 | 167 | 00A7 | connect sensor No. 19 address high bit |  | 0～65535
169 | 168 | 00A8 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
170 | 169 | 00A9 | Sensor 19 current |  | 0～65535(*0.1)
171 | 170 | 00AA | Sensor 19 temperature |  | 0～65535(*0.1)
172 | 171 | 00AB | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
173 | 172 | 00AC | current sensor count digit |  | 0～65535
174 | 173 | 00AD | reserved
175 | 174 | 00AE | Sensor 20 connection statue |  | 0～3600(second)
176 | 175 | 00AF | connect sensor No. 20 address low bit |  | 0～65535
177 | 176 | 00B0 | connect sensor No. 20 address high bit |  | 0～65535
178 | 177 | 00B1 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
179 | 178 | 00B2 | Sensor 20 current |  | 0～65535(*0.1)
180 | 179 | 00B3 | Sensor 20 temperature |  | 0～65535(*0.1)
181 | 180 | 00B4 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
182 | 181 | 00B5 | current sensor count digit |  | 0～65535
183 | 182 | 00B6 | reserved
184 | 183 | 00B7 | Sensor 21 connection statue |  | 0～3600(second)
185 | 184 | 00B8 | connect sensor No. 21 address low bit |  | 0～65535
186 | 185 | 00B9 | connect sensor No. 21 address high bit |  | 0～65535
187 | 186 | 00BA | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
188 | 187 | 00BB | Sensor 21 current |  | 0～65535(*0.1)
189 | 188 | 00BC | Sensor 21 temperature |  | 0～65535(*0.1)
190 | 189 | 00BD | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
191 | 190 | 00BE | current sensor count digit |  | 0～65535
192 | 191 | 00BF | reserved
193 | 192 | 00C0 | Sensor 22 connection statue |  | 0～3600(second)
194 | 193 | 00C1 | connect sensor No. 22 address low bit |  | 0～65535
195 | 194 | 00C2 | connect sensor No. 22 address high bit |  | 0～65535
196 | 195 | 00C3 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
197 | 196 | 00C4 | Sensor 22 current |  | 0～65535(*0.1)
198 | 197 | 00C5 | Sensor 22 temperature |  | 0～65535(*0.1)
199 | 198 | 00C6 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
200 | 199 | 00C7 | current sensor count digit |  | 0～65535
201 | 200 | 00C8 | reserved
202 | 201 | 00C9 | Sensor 23 connection statue |  | 0～3600(second)
203 | 202 | 00CA | connect sensor No. 23 address low bit |  | 0～65535
204 | 203 | 00CB | connect sensor No. 23 address high bit |  | 0～65535
205 | 204 | 00CC | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
206 | 205 | 00CD | Sensor 23 current |  | 0～65535(*0.1)
207 | 206 | 00CE | Sensor 23 temperature |  | 0～65535(*0.1)
208 | 207 | 00CF | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
209 | 208 | 00D0 | current sensor count digit |  | 0～65535
210 | 209 | 00D1 | reserved
211 | 210 | 00D2 | Sensor 24 connection statue |  | 0～3600(second)
212 | 211 | 00D3 | connect sensor No. 24 address low bit |  | 0～65535
213 | 212 | 00D4 | connect sensor No. 24 address high bit |  | 0～65535
214 | 213 | 00D5 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
215 | 214 | 00D6 | Sensor 24 current |  | 0～65535(*0.1)
216 | 215 | 00D7 | Sensor 24 temperature |  | 0～65535(*0.1)
217 | 216 | 00D8 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
218 | 217 | 00D9 | current sensor count digit |  | 0～65535
219 | 218 | 00DA | reserved
220 | 219 | 00DB | Sensor 25 connection statue |  | 0～3600(second)
221 | 220 | 00DC | connect sensor No. 25 address low bit |  | 0～65535
222 | 221 | 00DD | connect sensor No. 25 address high bit |  | 0～65535
223 | 222 | 00DE | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
224 | 223 | 00DF | Sensor 25 current |  | 0～65535(*0.1)
225 | 224 | 00E0 | Sensor 25 temperature |  | 0～65535(*0.1)
226 | 225 | 00E1 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
227 | 226 | 00E2 | current sensor count digit |  | 0～65535
228 | 227 | 00E3 | reserved
229 | 228 | 00E4 | Sensor 26 connection statue |  | 0～3600(second)
230 | 229 | 00E5 | connect sensor No. 26 address low bit |  | 0～65535
231 | 230 | 00E6 | connect sensor No. 26 address high bit |  | 0～65535
232 | 231 | 00E7 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
233 | 232 | 00E8 | Sensor 26 current |  | 0～65535(*0.1)
234 | 233 | 00E9 | Sensor 26 temperature |  | 0～65535(*0.1)
235 | 234 | 00EA | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
236 | 235 | 00EB | current sensor count digit |  | 0～65535
237 | 236 | 00EC | reserved
238 | 237 | 00ED | Sensor 27 connection statue |  | 0～3600(second)
239 | 238 | 00EE | connect sensor No. 27 address low bit |  | 0～65535
240 | 239 | 00EF | connect sensor No. 27 address high bit |  | 0～65535
241 | 240 | 00F0 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
242 | 241 | 00F1 | Sensor 27 current |  | 0～65535(*0.1)
243 | 242 | 00F2 | Sensor 27 temperature |  | 0～65535(*0.1)
244 | 243 | 00F3 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
245 | 244 | 00F4 | current sensor count digit |  | 0～65535
246 | 245 | 00F5 | reserved
247 | 246 | 00F6 | Sensor 28 connection statue |  | 0～3600(second)
248 | 247 | 00F7 | connect sensor No. 28 address low bit |  | 0～65535
249 | 248 | 00F8 | connect sensor No. 28 address high bit |  | 0～65535
250 | 249 | 00F9 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
251 | 250 | 00FA | Sensor 28 current |  | 0～65535(*0.1)
252 | 251 | 00FB | Sensor 28 temperature |  | 0～65535(*0.1)
253 | 252 | 00FC | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
254 | 253 | 00FD | current sensor count digit |  | 0～65535
255 | 254 | 00FE | reserved
256 | 255 | 00FF | Sensor 29 connection statue |  | 0～3600(second)
257 | 256 | 0100 | connect sensor No. 29 address low bit |  | 0～65535
258 | 257 | 0101 | connect sensor No. 29 address high bit |  | 0～65535
259 | 258 | 0102 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
260 | 259 | 0103 | Sensor 29 current |  | 0～65535(*0.1)
261 | 260 | 0104 | Sensor 29 temperature |  | 0～65535(*0.1)
262 | 261 | 0105 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
263 | 262 | 0106 | current sensor count digit |  | 0～65535
264 | 263 | 0107 | reserved
265 | 264 | 0108 | Sensor 30 connection statue |  | 0～3600(second)
266 | 265 | 0109 | connect sensor No. 30 address low bit |  | 0～65535
267 | 266 | 010A | connect sensor No. 30 address high bit |  | 0～65535
268 | 267 | 010B | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
269 | 268 | 010C | Sensor 30 current |  | 0～65535(*0.1)
270 | 269 | 010D | Sensor 30 temperature |  | 0～65535(*0.1)
271 | 270 | 010E | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
272 | 271 | 010F | current sensor count digit |  | 0～65535
273 | 272 | 0110 | reserved
274 | 273 | 0111 | Sensor 31 connection statue |  | 0～3600(second)
275 | 274 | 0112 | connect sensor No. 31 address low bit |  | 0～65535
276 | 275 | 0113 | connect sensor No. 31 address high bit |  | 0～65535
277 | 276 | 0114 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
278 | 277 | 0115 | Sensor 31 current |  | 0～65535(*0.1)
279 | 278 | 0116 | Sensor 31 temperature |  | 0～65535(*0.1)
280 | 279 | 0117 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
281 | 280 | 0118 | current sensor count digit |  | 0～65535
282 | 281 | 0119 | reserved
283 | 282 | 011A | Sensor 32 connection statue |  | 0～3600(second)
284 | 283 | 011B | connect sensor No. 32 address low bit |  | 0～65535
285 | 284 | 011C | connect sensor No. 32 address high bit |  | 0～65535
286 | 285 | 011D | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
287 | 286 | 011E | Sensor 32 current |  | 0～65535(*0.1)
288 | 287 | 011F | Sensor 32 temperature |  | 0～65535(*0.1)
289 | 288 | 0120 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
290 | 289 | 0121 | current sensor count digit |  | 0～65535
291 | 290 | 0122 | reserved
292 | 291 | 0123 | Sensor 33 connection statue |  | 0～3600(second)
293 | 292 | 0124 | connect sensor No. 33 address low bit |  | 0～65535
294 | 293 | 0125 | connect sensor No. 33 address high bit |  | 0～65535
295 | 294 | 0126 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
296 | 295 | 0127 | Sensor 33 current |  | 0～65535(*0.1)
297 | 296 | 0128 | Sensor 33 temperature |  | 0～65535(*0.1)
298 | 297 | 0129 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
299 | 298 | 012A | current sensor count digit |  | 0～65535
300 | 299 | 012B | reserved
301 | 300 | 012C | Sensor 34 connection statue |  | 0～3600(second)
302 | 301 | 012D | connect sensor No. 34 address low bit |  | 0～65535
303 | 302 | 012E | connect sensor No. 34 address high bit |  | 0～65535
304 | 303 | 012F | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
305 | 304 | 0130 | Sensor 34 current |  | 0～65535(*0.1)
306 | 305 | 0131 | Sensor 34 temperature |  | 0～65535(*0.1)
307 | 306 | 0132 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
308 | 307 | 0133 | current sensor count digit |  | 0～65535
309 | 308 | 0134 | reserved
310 | 309 | 0135 | Sensor 35 connection statue |  | 0～3600(second)
311 | 310 | 0136 | connect sensor No. 35 address low bit |  | 0～65535
312 | 311 | 0137 | connect sensor No. 35 address high bit |  | 0～65535
313 | 312 | 0138 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
314 | 313 | 0139 | Sensor 35 current |  | 0～65535(*0.1)
315 | 314 | 013A | Sensor 35 temperature |  | 0～65535(*0.1)
316 | 315 | 013B | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
317 | 316 | 013C | current sensor count digit |  | 0～65535
318 | 317 | 013D | reserved
319 | 318 | 013E | Sensor 36 connection statue |  | 0～3600(second)
320 | 319 | 013F | connect sensor No. 36 address low bit |  | 0～65535
321 | 320 | 0140 | connect sensor No. 36 address high bit |  | 0～65535
322 | 321 | 0141 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
323 | 322 | 0142 | Sensor 36 current |  | 0～65535(*0.1)
324 | 323 | 0143 | Sensor 36 temperature |  | 0～65535(*0.1)
325 | 324 | 0144 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
326 | 325 | 0145 | current sensor count digit |  | 0～65535
327 | 326 | 0146 | reserved
328 | 327 | 0147 | Sensor 37 connection statue |  | 0～3600(second)
329 | 328 | 0148 | connect sensor No. 37 address low bit |  | 0～65535
330 | 329 | 0149 | connect sensor No. 37 address high bit |  | 0～65535
331 | 330 | 014A | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
332 | 331 | 014B | Sensor 37 current |  | 0～65535(*0.1)
333 | 332 | 014C | Sensor 37 temperature |  | 0～65535(*0.1)
334 | 333 | 014D | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
335 | 334 | 014E | current sensor count digit |  | 0～65535
336 | 335 | 014F | reserved
337 | 336 | 0150 | Sensor 38 connection statue |  | 0～3600(second)
338 | 337 | 0151 | connect sensor No. 38 address low bit |  | 0～65535
339 | 338 | 0152 | connect sensor No. 38 address high bit |  | 0～65535
340 | 339 | 0153 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
341 | 340 | 0154 | Sensor 38 current |  | 0～65535(*0.1)
342 | 341 | 0155 | Sensor 38 temperature |  | 0～65535(*0.1)
343 | 342 | 0156 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
344 | 343 | 0157 | current sensor count digit |  | 0～65535
345 | 344 | 0158 | reserved
346 | 345 | 0159 | Sensor 39 connection statue |  | 0～3600(second)
347 | 346 | 015A | connect sensor No. 39 address low bit |  | 0～65535
348 | 347 | 015B | connect sensor No. 39 address high bit |  | 0～65535
349 | 348 | 015C | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
350 | 349 | 015D | Sensor 39 current |  | 0～65535(*0.1)
351 | 350 | 015E | Sensor 39 temperature |  | 0～65535(*0.1)
352 | 351 | 015F | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
353 | 352 | 0160 | current sensor count digit |  | 0～65535
354 | 353 | 0161 | reserved
355 | 354 | 0162 | Sensor 40 connection statue |  | 0～3600(second)
356 | 355 | 0163 | connect sensor No. 40 address low bit |  | 0～65535
357 | 356 | 0164 | connect sensor No. 40 address high bit |  | 0～65535
358 | 357 | 0165 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
359 | 358 | 0166 | Sensor 40 current |  | 0～65535(*0.1)
360 | 359 | 0167 | Sensor 40 temperature |  | 0～65535(*0.1)
361 | 360 | 0168 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
362 | 361 | 0169 | current sensor count digit |  | 0～65535
363 | 362 | 016A | reserved
364 | 363 | 016B | Sensor 41 connection statue |  | 0～3600(second)
365 | 364 | 016C | connect sensor No. 41 address low bit |  | 0～65535
366 | 365 | 016D | connect sensor No. 41 address high bit |  | 0～65535
367 | 366 | 016E | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
368 | 367 | 016F | Sensor 41 current |  | 0～65535(*0.1)
369 | 368 | 0170 | Sensor 41 temperature |  | 0～65535(*0.1)
370 | 369 | 0171 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
371 | 370 | 0172 | current sensor count digit |  | 0～65535
372 | 371 | 0173 | reserved
373 | 372 | 0174 | Sensor 42 connection statue |  | 0～3600(second)
374 | 373 | 0175 | connect sensor No. 42 address low bit |  | 0～65535
375 | 374 | 0176 | connect sensor No. 42 address high bit |  | 0～65535
376 | 375 | 0177 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
377 | 376 | 0178 | Sensor 42 current |  | 0～65535(*0.1)
378 | 377 | 0179 | Sensor 42 temperature |  | 0～65535(*0.1)
379 | 378 | 017A | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
380 | 379 | 017B | current sensor count digit |  | 0～65535
381 | 380 | 017C | reserved
382 | 381 | 017D | Sensor 43 connection statue |  | 0～3600(second)
383 | 382 | 017E | connect sensor No. 43 address low bit |  | 0～65535
384 | 383 | 017F | connect sensor No. 43 address high bit |  | 0～65535
385 | 384 | 0180 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
386 | 385 | 0181 | Sensor 43 current |  | 0～65535(*0.1)
387 | 386 | 0182 | Sensor 43 temperature |  | 0～65535(*0.1)
388 | 387 | 0183 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
389 | 388 | 0184 | current sensor count digit |  | 0～65535
390 | 389 | 0185 | reserved
391 | 390 | 0186 | Sensor 44 connection statue |  | 0～3600(second)
392 | 391 | 0187 | connect sensor No. 44 address low bit |  | 0～65535
393 | 392 | 0188 | connect sensor No. 44 address high bit |  | 0～65535
394 | 393 | 0189 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
395 | 394 | 018A | Sensor 44 current |  | 0～65535(*0.1)
396 | 395 | 018B | Sensor 44 temperature |  | 0～65535(*0.1)
397 | 396 | 018C | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
398 | 397 | 018D | current sensor count digit |  | 0～65535
399 | 398 | 018E | reserved
400 | 399 | 018F | Sensor 45 connection statue |  | 0～3600(second)
401 | 400 | 0190 | connect sensor No. 45 address low bit |  | 0～65535
402 | 401 | 0191 | connect sensor No. 45 address high bit |  | 0～65535
403 | 402 | 0192 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
404 | 403 | 0193 | Sensor 45 current |  | 0～65535(*0.1)
405 | 404 | 0194 | Sensor 45 temperature |  | 0～65535(*0.1)
406 | 405 | 0195 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
407 | 406 | 0196 | current sensor count digit |  | 0～65535
408 | 407 | 0197 | reserved
409 | 408 | 0198 | Sensor 46 connection statue |  | 0～3600(second)
410 | 409 | 0199 | connect sensor No. 46 address low bit |  | 0～65535
411 | 410 | 019A | connect sensor No. 46 address high bit |  | 0～65535
412 | 411 | 019B | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
413 | 412 | 019C | Sensor 46 current |  | 0～65535(*0.1)
414 | 413 | 019D | Sensor 46 temperature |  | 0～65535(*0.1)
415 | 414 | 019E | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
416 | 415 | 019F | current sensor count digit |  | 0～65535
417 | 416 | 01A0 | reserved
418 | 417 | 01A1 | Sensor 47 connection statue |  | 0～3600(second)
419 | 418 | 01A2 | connect sensor No. 47 address low bit |  | 0～65535
420 | 419 | 01A3 | connect sensor No. 47 address high bit |  | 0～65535
421 | 420 | 01A4 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
422 | 421 | 01A5 | Sensor 47 current |  | 0～65535(*0.1)
423 | 422 | 01A6 | Sensor 47 temperature |  | 0～65535(*0.1)
424 | 423 | 01A7 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
425 | 424 | 01A8 | current sensor count digit |  | 0～65535
426 | 425 | 01A9 | reserved
427 | 426 | 01AA | Sensor 48 connection statue |  | 0～3600(second)
428 | 427 | 01AB | connect sensor No. 48 address low bit |  | 0～65535
429 | 428 | 01AC | connect sensor No. 48 address high bit |  | 0～65535
430 | 429 | 01AD | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
431 | 430 | 01AE | Sensor 48 current |  | 0～65535(*0.1)
432 | 431 | 01AF | Sensor 48 temperature |  | 0～65535(*0.1)
433 | 432 | 01B0 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
434 | 433 | 01B1 | current sensor count digit |  | 0～65535
435 | 434 | 01B2 | reserved
436 | 435 | 01B3 | Sensor 49 connection statue |  | 0～3600(second)
437 | 436 | 01B4 | connect sensor No. 49 address low bit |  | 0～65535
438 | 437 | 01B5 | connect sensor No. 49 address high bit |  | 0～65535
439 | 438 | 01B6 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
440 | 439 | 01B7 | Sensor 49 current |  | 0～65535(*0.1)
441 | 440 | 01B8 | Sensor 49 temperature |  | 0～65535(*0.1)
442 | 441 | 01B9 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
443 | 442 | 01BA | current sensor count digit |  | 0～65535
444 | 443 | 01BB | reserved
445 | 444 | 01BC | Sensor 50 connection statue |  | 0～3600(second)
446 | 445 | 01BD | connect sensor No. 50 address low bit |  | 0～65535
447 | 446 | 01BE | connect sensor No. 50 address high bit |  | 0～65535
448 | 447 | 01BF | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
449 | 448 | 01C0 | Sensor 50 current |  | 0～65535(*0.1)
450 | 449 | 01C1 | Sensor 50 temperature |  | 0～65535(*0.1)
451 | 450 | 01C2 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
452 | 451 | 01C3 | current sensor count digit |  | 0～65535
453 | 452 | 01C4 | reserved
454 | 453 | 01C5 | Sensor 51 connection statue |  | 0～3600(second)
455 | 454 | 01C6 | connect sensor No. 51 address low bit |  | 0～65535
456 | 455 | 01C7 | connect sensor No. 51 address high bit |  | 0～65535
457 | 456 | 01C8 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
458 | 457 | 01C9 | Sensor 51 current |  | 0～65535(*0.1)
459 | 458 | 01CA | Sensor 51 temperature |  | 0～65535(*0.1)
460 | 459 | 01CB | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
461 | 460 | 01CC | current sensor count digit |  | 0～65535
462 | 461 | 01CD | reserved
463 | 462 | 01CE | Sensor 52 connection statue |  | 0～3600(second)
464 | 463 | 01CF | connect sensor No. 52 address low bit |  | 0～65535
465 | 464 | 01D0 | connect sensor No. 52 address high bit |  | 0～65535
466 | 465 | 01D1 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
467 | 466 | 01D2 | Sensor 52 current |  | 0～65535(*0.1)
468 | 467 | 01D3 | Sensor 52 temperature |  | 0～65535(*0.1)
469 | 468 | 01D4 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
470 | 469 | 01D5 | current sensor count digit |  | 0～65535
471 | 470 | 01D6 | reserved
472 | 471 | 01D7 | Sensor 53 connection statue |  | 0～3600(second)
473 | 472 | 01D8 | connect sensor No. 53 address low bit |  | 0～65535
474 | 473 | 01D9 | connect sensor No. 53 address high bit |  | 0～65535
475 | 474 | 01DA | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
476 | 475 | 01DB | Sensor 53 current |  | 0～65535(*0.1)
477 | 476 | 01DC | Sensor 53 temperature |  | 0～65535(*0.1)
478 | 477 | 01DD | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
479 | 478 | 01DE | current sensor count digit |  | 0～65535
480 | 479 | 01DF | reserved
481 | 480 | 01E0 | Sensor 54 connection statue |  | 0～3600(second)
482 | 481 | 01E1 | connect sensor No. 54 address low bit |  | 0～65535
483 | 482 | 01E2 | connect sensor No. 54 address high bit |  | 0～65535
484 | 483 | 01E3 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
485 | 484 | 01E4 | Sensor 54 current |  | 0～65535(*0.1)
486 | 485 | 01E5 | Sensor 54 temperature |  | 0～65535(*0.1)
487 | 486 | 01E6 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
488 | 487 | 01E7 | current sensor count digit |  | 0～65535
489 | 488 | 01E8 | reserved
490 | 489 | 01E9 | Sensor 55 connection statue |  | 0～3600(second)
491 | 490 | 01EA | connect sensor No. 55 address low bit |  | 0～65535
492 | 491 | 01EB | connect sensor No. 55 address high bit |  | 0～65535
493 | 492 | 01EC | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
494 | 493 | 01ED | Sensor 55 current |  | 0～65535(*0.1)
495 | 494 | 01EE | Sensor 55 temperature |  | 0～65535(*0.1)
496 | 495 | 01EF | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
497 | 496 | 01F0 | current sensor count digit |  | 0～65535
498 | 497 | 01F1 | reserved
499 | 498 | 01F2 | Sensor 56 connection statue |  | 0～3600(second)
500 | 499 | 01F3 | connect sensor No. 56 address low bit |  | 0～65535
501 | 500 | 01F4 | connect sensor No. 56 address high bit |  | 0～65535
502 | 501 | 01F5 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
503 | 502 | 01F6 | Sensor 56 current |  | 0～65535(*0.1)
504 | 503 | 01F7 | Sensor 56 temperature |  | 0～65535(*0.1)
505 | 504 | 01F8 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
506 | 505 | 01F9 | current sensor count digit |  | 0～65535
507 | 506 | 01FA | reserved
508 | 507 | 01FB | Sensor 57 connection statue |  | 0～3600(second)
509 | 508 | 01FC | connect sensor No. 57 address low bit |  | 0～65535
510 | 509 | 01FD | connect sensor No. 57 address high bit |  | 0～65535
511 | 510 | 01FE | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
512 | 511 | 01FF | Sensor 57 current |  | 0～65535(*0.1)
513 | 512 | 0200 | Sensor 57 temperature |  | 0～65535(*0.1)
514 | 513 | 0201 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
515 | 514 | 0202 | current sensor count digit |  | 0～65535
516 | 515 | 0203 | reserved
517 | 516 | 0204 | Sensor 58 connection statue |  | 0～3600(second)
518 | 517 | 0205 | connect sensor No. 58 address low bit |  | 0～65535
519 | 518 | 0206 | connect sensor No. 58 address high bit |  | 0～65535
520 | 519 | 0207 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
521 | 520 | 0208 | Sensor 58 current |  | 0～65535(*0.1)
522 | 521 | 0209 | Sensor 58 temperature |  | 0～65535(*0.1)
523 | 522 | 020A | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
524 | 523 | 020B | current sensor count digit |  | 0～65535
525 | 524 | 020C | reserved
526 | 525 | 020D | Sensor 59 connection statue |  | 0～3600(second)
527 | 526 | 020E | connect sensor No. 59 address low bit |  | 0～65535
528 | 527 | 020F | connect sensor No. 59 address high bit |  | 0～65535
529 | 528 | 0210 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
530 | 529 | 0211 | Sensor 59 current |  | 0～65535(*0.1)
531 | 530 | 0212 | Sensor 59 temperature |  | 0～65535(*0.1)
532 | 531 | 0213 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
533 | 532 | 0214 | current sensor count digit |  | 0～65535
534 | 533 | 0215 | reserved
535 | 534 | 0216 | Sensor 60 connection statue |  | 0～3600(second)
536 | 535 | 0217 | connect sensor No. 60 address low bit |  | 0～65535
537 | 536 | 0218 | connect sensor No. 60 address high bit |  | 0～65535
538 | 537 | 0219 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
539 | 538 | 021A | Sensor 60 current |  | 0～65535(*0.1)
540 | 539 | 021B | Sensor 60 temperature |  | 0～65535(*0.1)
541 | 540 | 021C | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
542 | 541 | 021D | current sensor count digit |  | 0～65535
543 | 542 | 021E | reserved
544 | 543 | 021F | Sensor 61 connection statue |  | 0～3600(second)
545 | 544 | 0220 | connect sensor No. 61 address low bit |  | 0～65535
546 | 545 | 0221 | connect sensor No. 61 address high bit |  | 0～65535
547 | 546 | 0222 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
548 | 547 | 0223 | Sensor 61 current |  | 0～65535(*0.1)
549 | 548 | 0224 | Sensor 61 temperature |  | 0～65535(*0.1)
550 | 549 | 0225 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
551 | 550 | 0226 | current sensor count digit |  | 0～65535
552 | 551 | 0227 | reserved
553 | 552 | 0228 | Sensor 62 connection statue |  | 0～3600(second)
554 | 553 | 0229 | connect sensor No. 62 address low bit |  | 0～65535
555 | 554 | 022A | connect sensor No. 62 address high bit |  | 0～65535
556 | 555 | 022B | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
557 | 556 | 022C | Sensor 62 current |  | 0～65535(*0.1)
558 | 557 | 022D | Sensor 62 temperature |  | 0～65535(*0.1)
559 | 558 | 022E | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
560 | 559 | 022F | current sensor count digit |  | 0～65535
561 | 560 | 0230 | reserved
562 | 561 | 0231 | Sensor 63 connection statue |  | 0～3600(second)
563 | 562 | 0232 | connect sensor No. 63 address low bit |  | 0～65535
564 | 563 | 0233 | connect sensor No. 63 address high bit |  | 0～65535
565 | 564 | 0234 | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
566 | 565 | 0235 | Sensor 63 current |  | 0～65535(*0.1)
567 | 566 | 0236 | Sensor 63 temperature |  | 0～65535(*0.1)
568 | 567 | 0237 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
569 | 568 | 0238 | current sensor count digit |  | 0～65535
570 | 569 | 0239 | reserved
571 | 570 | 023A | Sensor 64 connection statue |  | 0～3600(second)
572 | 571 | 023B | connect sensor No. 64 address low bit |  | 0～65535
573 | 572 | 023C | connect sensor No. 64 address high bit |  | 0～65535
574 | 573 | 023D | high byte: sensor wireless signal strength low byte: sensor data statue |  | high byte：-128～128 low byte：（0：not received value or offline；1：0;2：2～10；3：>10；）
575 | 574 | 023E | Sensor 64 current |  | 0～65535(*0.1)
576 | 575 | 023F | Sensor 64 temperature |  | 0～65535(*0.1)
577 | 576 | 0240 | check flag bit |  | 0～65535 （0 bit: open/close measuring statue: close: 0 open:1； 1 bit: battery low battery:1， Normal Battery: 0）
578 | 577 | 0241 | current sensor count digit |  | 0～65535
579 | 578 | 0242 | reserved

## Basic Parameters Automatic Mode
Basic Parameters at Automatic mode (function code 04 read)
No. | address Decimal | Address Hexadecimal | Name | Default | Range（Big Endian）
1 | 4096 | 1000 | Connected Slave Sensor QTY at Automatic mode | 0 | 0～64
2 | 4097 | 1001 | Connected Slave Sensor No. 1 address low bit | 0 | 0～65535
3 | 4098 | 1002 | Connected Slave Sensor No. 1 address high bit | 0 | 0～65535
4 | 4099 | 1003 | Connected Slave Sensor No. 2 address low bit | 0 | 0～65535
5 | 4100 | 1004 | Connected Slave Sensor No. 2 address high bit | 0 | 0～65535
6 | 4101 | 1005 | Connected Slave Sensor No. 3 address low bit | 0 | 0～65535
7 | 4102 | 1006 | Connected Slave Sensor No. 3 address high bit | 0 | 0～65535
8 | 4103 | 1007 | Connected Slave Sensor No. 4 address low bit | 0 | 0～65535
9 | 4104 | 1008 | Connected Slave Sensor No. 4 address high bit | 0 | 0～65535
10 | 4105 | 1009 | Connected Slave Sensor No. 5 address low bit | 0 | 0～65535
11 | 4106 | 100A | Connected Slave Sensor No. 5 address high bit | 0 | 0～65535
12 | 4107 | 100B | Connected Slave Sensor No. 6 address low bit | 0 | 0～65535
13 | 4108 | 100C | Connected Slave Sensor No. 6 address high bit | 0 | 0～65535
14 | 4109 | 100D | Connected Slave Sensor No. 7 address low bit | 0 | 0～65535
15 | 4110 | 100E | Connected Slave Sensor No. 7 address high bit | 0 | 0～65535
16 | 4111 | 100F | Connected Slave Sensor No. 8 address low bit | 0 | 0～65535
17 | 4112 | 1010 | Connected Slave Sensor No. 8 address high bit | 0 | 0～65535
18 | 4113 | 1011 | Connected Slave Sensor No. 9 address low bit | 0 | 0～65535
19 | 4114 | 1012 | Connected Slave Sensor No. 9 address high bit | 0 | 0～65535
20 | 4115 | 1013 | Connected Slave Sensor No. 10 address low bit | 0 | 0～65535
21 | 4116 | 1014 | Connected Slave Sensor No. 10 address high bit | 0 | 0～65535
22 | 4117 | 1015 | Connected Slave Sensor No. 11 address low bit | 0 | 0～65535
23 | 4118 | 1016 | Connected Slave Sensor No. 11 address high bit | 0 | 0～65535
24 | 4119 | 1017 | Connected Slave Sensor No. 12 address low bit | 0 | 0～65535
25 | 4120 | 1018 | Connected Slave Sensor No. 12 address high bit | 0 | 0～65535
26 | 4121 | 1019 | Connected Slave Sensor No. 13 address low bit | 0 | 0～65535
27 | 4122 | 101A | Connected Slave Sensor No. 13 address high bit | 0 | 0～65535
28 | 4123 | 101B | Connected Slave Sensor No. 14 address low bit | 0 | 0～65535
29 | 4124 | 101C | Connected Slave Sensor No. 14 address high bit | 0 | 0～65535
30 | 4125 | 101D | Connected Slave Sensor No. 15 address low bit | 0 | 0～65535
31 | 4126 | 101E | Connected Slave Sensor No. 15 address high bit | 0 | 0～65535
32 | 4127 | 101F | Connected Slave Sensor No. 16 address low bit | 0 | 0～65535
33 | 4128 | 1020 | Connected Slave Sensor No. 16 address high bit | 0 | 0～65535
34 | 4129 | 1021 | Connected Slave Sensor No. 17 address low bit | 0 | 0～65535
35 | 4130 | 1022 | Connected Slave Sensor No. 17 address high bit | 0 | 0～65535
36 | 4131 | 1023 | Connected Slave Sensor No. 18 address low bit | 0 | 0～65535
37 | 4132 | 1024 | Connected Slave Sensor No. 18 address high bit | 0 | 0～65535
38 | 4133 | 1025 | Connected Slave Sensor No. 19 address low bit | 0 | 0～65535
39 | 4134 | 1026 | Connected Slave Sensor No. 19 address high bit | 0 | 0～65535
40 | 4135 | 1027 | Connected Slave Sensor No. 20 address low bit | 0 | 0～65535
41 | 4136 | 1028 | Connected Slave Sensor No. 20 address high bit | 0 | 0～65535
42 | 4137 | 1029 | Connected Slave Sensor No. 21 address low bit | 0 | 0～65535
43 | 4138 | 102A | Connected Slave Sensor No. 21 address high bit | 0 | 0～65535
44 | 4139 | 102B | Connected Slave Sensor No. 22 address low bit | 0 | 0～65535
45 | 4140 | 102C | Connected Slave Sensor No. 22 address high bit | 0 | 0～65535
46 | 4141 | 102D | Connected Slave Sensor No. 23 address low bit | 0 | 0～65535
47 | 4142 | 102E | Connected Slave Sensor No. 23 address high bit | 0 | 0～65535
48 | 4143 | 102F | Connected Slave Sensor No. 24 address low bit | 0 | 0～65535
49 | 4144 | 1030 | Connected Slave Sensor No. 24 address high bit | 0 | 0～65535
50 | 4145 | 1031 | Connected Slave Sensor No. 25 address low bit | 0 | 0～65535
51 | 4146 | 1032 | Connected Slave Sensor No. 25 address high bit | 0 | 0～65535
52 | 4147 | 1033 | Connected Slave Sensor No. 26 address low bit | 0 | 0～65535
53 | 4148 | 1034 | Connected Slave Sensor No. 26 address high bit | 0 | 0～65535
54 | 4149 | 1035 | Connected Slave Sensor No. 27 address low bit | 0 | 0～65535
55 | 4150 | 1036 | Connected Slave Sensor No. 27 address high bit | 0 | 0～65535
56 | 4151 | 1037 | Connected Slave Sensor No. 28 address low bit | 0 | 0～65535
57 | 4152 | 1038 | Connected Slave Sensor No. 28 address high bit | 0 | 0～65535
58 | 4153 | 1039 | Connected Slave Sensor No. 29 address low bit | 0 | 0～65535
59 | 4154 | 103A | Connected Slave Sensor No. 29 address high bit | 0 | 0～65535
60 | 4155 | 103B | Connected Slave Sensor No. 30 address low bit | 0 | 0～65535
61 | 4156 | 103C | Connected Slave Sensor No. 30 address high bit | 0 | 0～65535
62 | 4157 | 103D | Connected Slave Sensor No. 31 address low bit | 0 | 0～65535
63 | 4158 | 103E | Connected Slave Sensor No. 31 address high bit | 0 | 0～65535
64 | 4159 | 103F | Connected Slave Sensor No. 32 address low bit | 0 | 0～65535
65 | 4160 | 1040 | Connected Slave Sensor No. 32 address high bit | 0 | 0～65535
66 | 4161 | 1041 | Connected Slave Sensor No. 33 address low bit | 0 | 0～65535
67 | 4162 | 1042 | Connected Slave Sensor No. 33 address high bit | 0 | 0～65535
68 | 4163 | 1043 | Connected Slave Sensor No. 34 address low bit | 0 | 0～65535
69 | 4164 | 1044 | Connected Slave Sensor No. 34 address high bit | 0 | 0～65535
70 | 4165 | 1045 | Connected Slave Sensor No. 35 address low bit | 0 | 0～65535
71 | 4166 | 1046 | Connected Slave Sensor No. 35 address high bit | 0 | 0～65535
72 | 4167 | 1047 | Connected Slave Sensor No. 36 address low bit | 0 | 0～65535
73 | 4168 | 1048 | Connected Slave Sensor No. 36 address high bit | 0 | 0～65535
74 | 4169 | 1049 | Connected Slave Sensor No. 37 address low bit | 0 | 0～65535
75 | 4170 | 104A | Connected Slave Sensor No. 37 address high bit | 0 | 0～65535
76 | 4171 | 104B | Connected Slave Sensor No. 38 address low bit | 0 | 0～65535
77 | 4172 | 104C | Connected Slave Sensor No. 38 address high bit | 0 | 0～65535
78 | 4173 | 104D | Connected Slave Sensor No. 39 address low bit | 0 | 0～65535
79 | 4174 | 104E | Connected Slave Sensor No. 39 address high bit | 0 | 0～65535
80 | 4175 | 104F | Connected Slave Sensor No. 40 address low bit | 0 | 0～65535
81 | 4176 | 1050 | Connected Slave Sensor No. 40 address high bit | 0 | 0～65535
82 | 4177 | 1051 | Connected Slave Sensor No. 41 address low bit | 0 | 0～65535
83 | 4178 | 1052 | Connected Slave Sensor No. 41 address high bit | 0 | 0～65535
84 | 4179 | 1053 | Connected Slave Sensor No. 42 address low bit | 0 | 0～65535
85 | 4180 | 1054 | Connected Slave Sensor No. 42 address high bit | 0 | 0～65535
86 | 4181 | 1055 | Connected Slave Sensor No. 43 address low bit | 0 | 0～65535
87 | 4182 | 1056 | Connected Slave Sensor No. 43 address high bit | 0 | 0～65535
88 | 4183 | 1057 | Connected Slave Sensor No. 44 address low bit | 0 | 0～65535
89 | 4184 | 1058 | Connected Slave Sensor No. 44 address high bit | 0 | 0～65535
90 | 4185 | 1059 | Connected Slave Sensor No. 45 address low bit | 0 | 0～65535
91 | 4186 | 105A | Connected Slave Sensor No. 45 address high bit | 0 | 0～65535
92 | 4187 | 105B | Connected Slave Sensor No. 46 address low bit | 0 | 0～65535
93 | 4188 | 105C | Connected Slave Sensor No. 46 address high bit | 0 | 0～65535
94 | 4189 | 105D | Connected Slave Sensor No. 47 address low bit | 0 | 0～65535
95 | 4190 | 105E | Connected Slave Sensor No. 47 address high bit | 0 | 0～65535
96 | 4191 | 105F | Connected Slave Sensor No. 48 address low bit | 0 | 0～65535
97 | 4192 | 1060 | Connected Slave Sensor No. 48 address high bit | 0 | 0～65535
98 | 4193 | 1061 | Connected Slave Sensor No. 49 address low bit | 0 | 0～65535
99 | 4194 | 1062 | Connected Slave Sensor No. 49 address high bit | 0 | 0～65535
100 | 4195 | 1063 | Connected Slave Sensor No. 50 address low bit | 0 | 0～65535
101 | 4196 | 1064 | Connected Slave Sensor No. 50 address high bit | 0 | 0～65535
102 | 4197 | 1065 | Connected Slave Sensor No. 51 address low bit | 0 | 0～65535
103 | 4198 | 1066 | Connected Slave Sensor No. 51 address high bit | 0 | 0～65535
104 | 4199 | 1067 | Connected Slave Sensor No. 52 address low bit | 0 | 0～65535
105 | 4200 | 1068 | Connected Slave Sensor No. 52 address high bit | 0 | 0～65535
106 | 4201 | 1069 | Connected Slave Sensor No. 53 address low bit | 0 | 0～65535
107 | 4202 | 106A | Connected Slave Sensor No. 53 address high bit | 0 | 0～65535
108 | 4203 | 106B | Connected Slave Sensor No. 54 address low bit | 0 | 0～65535
109 | 4204 | 106C | Connected Slave Sensor No. 54 address high bit | 0 | 0～65535
110 | 4205 | 106D | Connected Slave Sensor No. 55 address low bit | 0 | 0～65535
111 | 4206 | 106E | Connected Slave Sensor No. 55 address high bit | 0 | 0～65535
112 | 4207 | 106F | Connected Slave Sensor No. 56 address low bit | 0 | 0～65535
113 | 4208 | 1070 | Connected Slave Sensor No. 56 address high bit | 0 | 0～65535
114 | 4209 | 1071 | Connected Slave Sensor No. 57 address low bit | 0 | 0～65535
115 | 4210 | 1072 | Connected Slave Sensor No. 57 address high bit | 0 | 0～65535
116 | 4211 | 1073 | Connected Slave Sensor No. 58 address low bit | 0 | 0～65535
117 | 4212 | 1074 | Connected Slave Sensor No. 58 address high bit | 0 | 0～65535
118 | 4213 | 1075 | Connected Slave Sensor No. 59 address low bit | 0 | 0～65535
119 | 4214 | 1076 | Connected Slave Sensor No. 59 address high bit | 0 | 0～65535
120 | 4215 | 1077 | Connected Slave Sensor No. 60 address low bit | 0 | 0～65535
121 | 4216 | 1078 | Connected Slave Sensor No. 60 address high bit | 0 | 0～65535
122 | 4217 | 1079 | Connected Slave Sensor No. 61 address low bit | 0 | 0～65535
123 | 4218 | 107A | Connected Slave Sensor No. 61 address high bit | 0 | 0～65535
124 | 4219 | 107B | Connected Slave Sensor No. 62 address low bit | 0 | 0～65535
125 | 4220 | 107C | Connected Slave Sensor No. 62 address high bit | 0 | 0～65535
126 | 4221 | 107D | Connected Slave Sensor No. 63 address low bit | 0 | 0～65535
127 | 4222 | 107E | Connected Slave Sensor No. 63 address high bit | 0 | 0～65535
128 | 4223 | 107F | Connected Slave Sensor No. 64 address low bit | 0 | 0～65535
129 | 4224 | 1080 | Connected Slave Sensor No. 64 address high bit | 0 | 0～65535

## Basic Parameters at Manual Mode
Basic Parameter(function code 03 read,06/10 write)
No. | address Decimal | address Hexadecimal | Name | Default | Range（Big Endian）
1 | 8192 | 2000 | Slave Sensor No. address | 1 | 1～247（0 is broadcast address）
2 | 8193 | 2001 | Slave Sensor No. work Mode | 0 | 0～1（0：Automatic mode；1：Manual Mode）
3 | 8194 | 2002 | RS485-1 parity | 0 | 0～2（0：8N1；1:8E1；2:8O1）
4 | 8195 | 2003 | RS485-2 parity | 0 | 0～2（0：8N1；1:8E1；2:8O1）
5 | 8196 | 2004 | RS485-1 baud rate | 3 | 1～7（1:2400；2:4800；3：9600；4:19200；5:38400；6:57600；7:115200）
6 | 8197 | 2005 | RS485-2 baud rate | 3 | 1～7（1:2400；2:4800；3：9600；4:19200；5:38400；6:57600；7:115200）
7 | 8198 | 2006 | Slave Sensor No. 0-15 shielding flag | 0 | 0-65535（from low to high 1: shielding，0: open）
8 | 8199 | 2007 | Slave Sensor No. 16-31 shielding flag | 0 | 0-65535（from low to high 1: shielding，0: open）
9 | 8200 | 2008 | Slave Sensor No. 32-47 shielding flag | 0 | 0-65535（from low to high 1: shielding，0: open）
10 | 8201 | 2009 | Slave Sensor No. 48-63 shielding flag | 0 | 0-65535（from low to high 1: shielding，0: open）
11 | 8202 | 200A | IP domain name flag | 0 | 0-1（0: IP mode；1: domain name mode）
12 | 8203 | 200B | reserved
13 | 8204 | 200C
14 | 8205 | 200D | target port No. | 1883 | 0-65535
15 | 8206 | 200E | Alarm message push interval | 50 | 10-9999（s）
16 | 8207 | 200F | push interval | 60 | 1-600（s）
17 | 8208 | 2010 | Qos | 2 | 0-2
Basic Parameters at Manual Mode (function code 03 read,06/10 write)
No. | address Decimal | address Hexadecimal | Name | Default | Range（Big Endian）
1 | 8448 | 2100 | Connect Slave Sensor QTY | 0 | 0～64
2 | 8449 | 2101 | connect Slave Sensor No. 1 address low bit | 0 | 0～65535
3 | 8450 | 2102 | connect Slave Sensor No. 1 address high bit | 0 | 0～65535
4 | 8451 | 2103 | connect Slave Sensor No. 2 address low bit | 0 | 0～65535
5 | 8452 | 2104 | connect Slave Sensor No. 2 address high bit | 0 | 0～65535
6 | 8453 | 2105 | connect Slave Sensor No. 3 address low bit | 0 | 0～65535
7 | 8454 | 2106 | connect Slave Sensor No. 3 address high bit | 0 | 0～65535
8 | 8455 | 2107 | connect Slave Sensor No. 4 address low bit | 0 | 0～65535
9 | 8456 | 2108 | connect Slave Sensor No. 4 address high bit | 0 | 0～65535
10 | 8457 | 2109 | connect Slave Sensor No. 5 address low bit | 0 | 0～65535
11 | 8458 | 210A | connect Slave Sensor No. 5 address high bit | 0 | 0～65535
12 | 8459 | 210B | connect Slave Sensor No. 6 address low bit | 0 | 0～65535
13 | 8460 | 210C | connect Slave Sensor No. 6 address high bit | 0 | 0～65535
14 | 8461 | 210D | connect Slave Sensor No. 7 address low bit | 0 | 0～65535
15 | 8462 | 210E | connect Slave Sensor No. 7 address high bit | 0 | 0～65535
16 | 8463 | 210F | connect Slave Sensor No. 8 address low bit | 0 | 0～65535
17 | 8464 | 2110 | connect Slave Sensor No. 8 address high bit | 0 | 0～65535
18 | 8465 | 2111 | connect Slave Sensor No. 9 address low bit | 0 | 0～65535
19 | 8466 | 2112 | connect Slave Sensor No. 9 address high bit | 0 | 0～65535
20 | 8467 | 2113 | connect Slave Sensor No. 10 address low bit | 0 | 0～65535
21 | 8468 | 2114 | connect Slave Sensor No. 10 address high bit | 0 | 0～65535
22 | 8469 | 2115 | connect Slave Sensor No. 11 address low bit | 0 | 0～65535
23 | 8470 | 2116 | connect Slave Sensor No. 11 address high bit | 0 | 0～65535
24 | 8471 | 2117 | connect Slave Sensor No. 12 address low bit | 0 | 0～65535
25 | 8472 | 2118 | connect Slave Sensor No. 12 address high bit | 0 | 0～65535
26 | 8473 | 2119 | connect Slave Sensor No. 13 address low bit | 0 | 0～65535
27 | 8474 | 211A | connect Slave Sensor No. 13 address high bit | 0 | 0～65535
28 | 8475 | 211B | connect Slave Sensor No. 14 address low bit | 0 | 0～65535
29 | 8476 | 211C | connect Slave Sensor No. 14 address high bit | 0 | 0～65535
30 | 8477 | 211D | connect Slave Sensor No. 15 address low bit | 0 | 0～65535
31 | 8478 | 211E | connect Slave Sensor No. 15 address high bit | 0 | 0～65535
32 | 8479 | 211F | connect Slave Sensor No. 16 address low bit | 0 | 0～65535
33 | 8480 | 2120 | connect Slave Sensor No. 16 address high bit | 0 | 0～65535
34 | 8481 | 2121 | connect Slave Sensor No. 17 address low bit | 0 | 0～65535
35 | 8482 | 2122 | connect Slave Sensor No. 17 address high bit | 0 | 0～65535
36 | 8483 | 2123 | connect Slave Sensor No. 18 address low bit | 0 | 0～65535
37 | 8484 | 2124 | connect Slave Sensor No. 18 address high bit | 0 | 0～65535
38 | 8485 | 2125 | connect Slave Sensor No. 19 address low bit | 0 | 0～65535
39 | 8486 | 2126 | connect Slave Sensor No. 19 address high bit | 0 | 0～65535
40 | 8487 | 2127 | connect Slave Sensor No. 20 address low bit | 0 | 0～65535
41 | 8488 | 2128 | connect Slave Sensor No. 20 address high bit | 0 | 0～65535
42 | 8489 | 2129 | connect Slave Sensor No. 21 address low bit | 0 | 0～65535
43 | 8490 | 212A | connect Slave Sensor No. 21 address high bit | 0 | 0～65535
44 | 8491 | 212B | connect Slave Sensor No. 22 address low bit | 0 | 0～65535
45 | 8492 | 212C | connect Slave Sensor No. 22 address high bit | 0 | 0～65535
46 | 8493 | 212D | connect Slave Sensor No. 23 address low bit | 0 | 0～65535
47 | 8494 | 212E | connect Slave Sensor No. 23 address high bit | 0 | 0～65535
48 | 8495 | 212F | connect Slave Sensor No. 24 address low bit | 0 | 0～65535
49 | 8496 | 2130 | connect Slave Sensor No. 24 address high bit | 0 | 0～65535
50 | 8497 | 2131 | connect Slave Sensor No. 25 address low bit | 0 | 0～65535
51 | 8498 | 2132 | connect Slave Sensor No. 25 address high bit | 0 | 0～65535
52 | 8499 | 2133 | connect Slave Sensor No. 26 address low bit | 0 | 0～65535
53 | 8500 | 2134 | connect Slave Sensor No. 26 address high bit | 0 | 0～65535
54 | 8501 | 2135 | connect Slave Sensor No. 27 address low bit | 0 | 0～65535
55 | 8502 | 2136 | connect Slave Sensor No. 27 address high bit | 0 | 0～65535
56 | 8503 | 2137 | connect Slave Sensor No. 28 address low bit | 0 | 0～65535
57 | 8504 | 2138 | connect Slave Sensor No. 28 address high bit | 0 | 0～65535
58 | 8505 | 2139 | connect Slave Sensor No. 29 address low bit | 0 | 0～65535
59 | 8506 | 213A | connect Slave Sensor No. 29 address high bit | 0 | 0～65535
60 | 8507 | 213B | connect Slave Sensor No. 30 address low bit | 0 | 0～65535
61 | 8508 | 213C | connect Slave Sensor No. 30 address high bit | 0 | 0～65535
62 | 8509 | 213D | connect Slave Sensor No. 31 address low bit | 0 | 0～65535
63 | 8510 | 213E | connect Slave Sensor No. 31 address high bit | 0 | 0～65535
64 | 8511 | 213F | connect Slave Sensor No. 32 address low bit | 0 | 0～65535
65 | 8512 | 2140 | connect Slave Sensor No. 32 address high bit | 0 | 0～65535
66 | 8513 | 2141 | connect Slave Sensor No. 33 address low bit | 0 | 0～65535
67 | 8514 | 2142 | connect Slave Sensor No. 33 address high bit | 0 | 0～65535
68 | 8515 | 2143 | connect Slave Sensor No. 34 address low bit | 0 | 0～65535
69 | 8516 | 2144 | connect Slave Sensor No. 34 address high bit | 0 | 0～65535
70 | 8517 | 2145 | connect Slave Sensor No. 35 address low bit | 0 | 0～65535
71 | 8518 | 2146 | connect Slave Sensor No. 35 address high bit | 0 | 0～65535
72 | 8519 | 2147 | connect Slave Sensor No. 36 address low bit | 0 | 0～65535
73 | 8520 | 2148 | connect Slave Sensor No. 36 address high bit | 0 | 0～65535
74 | 8521 | 2149 | connect Slave Sensor No. 37 address low bit | 0 | 0～65535
75 | 8522 | 214A | connect Slave Sensor No. 37 address high bit | 0 | 0～65535
76 | 8523 | 214B | connect Slave Sensor No. 38 address low bit | 0 | 0～65535
77 | 8524 | 214C | connect Slave Sensor No. 38 address high bit | 0 | 0～65535
78 | 8525 | 214D | connect Slave Sensor No. 39 address low bit | 0 | 0～65535
79 | 8526 | 214E | connect Slave Sensor No. 39 address high bit | 0 | 0～65535
80 | 8527 | 214F | connect Slave Sensor No. 40 address low bit | 0 | 0～65535
81 | 8528 | 2150 | connect Slave Sensor No. 40 address high bit | 0 | 0～65535
82 | 8529 | 2151 | connect Slave Sensor No. 41 address low bit | 0 | 0～65535
83 | 8530 | 2152 | connect Slave Sensor No. 41 address high bit | 0 | 0～65535
84 | 8531 | 2153 | connect Slave Sensor No. 42 address low bit | 0 | 0～65535
85 | 8532 | 2154 | connect Slave Sensor No. 42 address high bit | 0 | 0～65535
86 | 8533 | 2155 | connect Slave Sensor No. 43 address low bit | 0 | 0～65535
87 | 8534 | 2156 | connect Slave Sensor No. 43 address high bit | 0 | 0～65535
88 | 8535 | 2157 | connect Slave Sensor No. 44 address low bit | 0 | 0～65535
89 | 8536 | 2158 | connect Slave Sensor No. 44 address high bit | 0 | 0～65535
90 | 8537 | 2159 | connect Slave Sensor No. 45 address low bit | 0 | 0～65535
91 | 8538 | 215A | connect Slave Sensor No. 45 address high bit | 0 | 0～65535
92 | 8539 | 215B | connect Slave Sensor No. 46 address low bit | 0 | 0～65535
93 | 8540 | 215C | connect Slave Sensor No. 46 address high bit | 0 | 0～65535
94 | 8541 | 215D | connect Slave Sensor No. 47 address low bit | 0 | 0～65535
95 | 8542 | 215E | connect Slave Sensor No. 47 address high bit | 0 | 0～65535
96 | 8543 | 215F | connect Slave Sensor No. 48 address low bit | 0 | 0～65535
97 | 8544 | 2160 | connect Slave Sensor No. 48 address high bit | 0 | 0～65535
98 | 8545 | 2161 | connect Slave Sensor No. 49 address low bit | 0 | 0～65535
99 | 8546 | 2162 | connect Slave Sensor No. 49 address high bit | 0 | 0～65535
100 | 8547 | 2163 | connect Slave Sensor No. 50 address low bit | 0 | 0～65535
101 | 8548 | 2164 | connect Slave Sensor No. 50 address high bit | 0 | 0～65535
102 | 8549 | 2165 | connect Slave Sensor No. 51 address low bit | 0 | 0～65535
103 | 8550 | 2166 | connect Slave Sensor No. 51 address high bit | 0 | 0～65535
104 | 8551 | 2167 | connect Slave Sensor No. 52 address low bit | 0 | 0～65535
105 | 8552 | 2168 | connect Slave Sensor No. 52 address high bit | 0 | 0～65535
106 | 8553 | 2169 | connect Slave Sensor No. 53 address low bit | 0 | 0～65535
107 | 8554 | 216A | connect Slave Sensor No. 53 address high bit | 0 | 0～65535
108 | 8555 | 216B | connect Slave Sensor No. 54 address low bit | 0 | 0～65535
109 | 8556 | 216C | connect Slave Sensor No. 54 address high bit | 0 | 0～65535
110 | 8557 | 216D | connect Slave Sensor No. 55 address low bit | 0 | 0～65535
111 | 8558 | 216E | connect Slave Sensor No. 55 address high bit | 0 | 0～65535
112 | 8559 | 216F | connect Slave Sensor No. 56 address low bit | 0 | 0～65535
113 | 8560 | 2170 | connect Slave Sensor No. 56 address high bit | 0 | 0～65535
114 | 8561 | 2171 | connect Slave Sensor No. 57 address low bit | 0 | 0～65535
115 | 8562 | 2172 | connect Slave Sensor No. 57 address high bit | 0 | 0～65535
116 | 8563 | 2173 | connect Slave Sensor No. 58 address low bit | 0 | 0～65535
117 | 8564 | 2174 | connect Slave Sensor No. 58 address high bit | 0 | 0～65535
118 | 8565 | 2175 | connect Slave Sensor No. 59 address low bit | 0 | 0～65535
119 | 8566 | 2176 | connect Slave Sensor No. 59 address high bit | 0 | 0～65535
120 | 8567 | 2177 | connect Slave Sensor No. 60 address low bit | 0 | 0～65535
121 | 8568 | 2178 | connect Slave Sensor No. 60 address high bit | 0 | 0～65535
122 | 8569 | 2179 | connect Slave Sensor No. 61 address low bit | 0 | 0～65535
123 | 8570 | 217A | connect Slave Sensor No. 61 address high bit | 0 | 0～65535
124 | 8571 | 217B | connect Slave Sensor No. 62 address low bit | 0 | 0～65535
125 | 8572 | 217C | connect Slave Sensor No. 62 address high bit | 0 | 0～65535
126 | 8573 | 217D | connect Slave Sensor No. 63 address low bit | 0 | 0～65535
127 | 8574 | 217E | connect Slave Sensor No. 63 address high bit | 0 | 0～65535
128 | 8575 | 217F | connect Slave Sensor No. 64 address low bit | 0 | 0～65535
129 | 8576 | 2180 | connect Slave Sensor No. 64 address high bit | 0 | 0～65535
Command：AA 10 2100 0005 0A 0002 0006 2190 0007 2190 CRCL CRCH AA is master Slave Sensor No. address, slave Slave Sensor No. address is 21900006,21900007.
1 | 9728 | 2600 | 域名第1个数字/字母 | www.hydiandangjia.com | 0-127 | 以ascii形式输入最高域名支持64个ascii字符 密支持32个ascii字符如位数少于最大支持位则以十进制0作为结束
2 | 9729 | 2601 | 域名第2个数字/字母 |  | 0-127
3 | 9730 | 2602 | 域名第3个数字/字母 |  | 0-127
4 | 9731 | 2603 | 域名第4个数字/字母 |  | 0-127
5 | 9732 | 2604 | 域名第5个数字/字母 |  | 0-127
6 | 9733 | 2605 | 域名第6个数字/字母 |  | 0-127
7 | 9734 | 2606 | 域名第7个数字/字母 |  | 0-127
8 | 9735 | 2607 | 域名第8个数字/字母 |  | 0-127
9 | 9736 | 2608 | 域名第9个数字/字母 |  | 0-127
10 | 9737 | 2609 | 域名第10个数字/字母 |  | 0-127
11 | 9738 | 260A | 域名第11个数字/字母 |  | 0-127
12 | 9739 | 260B | 域名第12个数字/字母 |  | 0-127
13 | 9740 | 260C | 域名第13个数字/字母 |  | 0-127
14 | 9741 | 260D | 域名第14个数字/字母 |  | 0-127
15 | 9742 | 260E | 域名第15个数字/字母 |  | 0-127
16 | 9743 | 260F | 域名第16个数字/字母 |  | 0-127
17 | 9744 | 2610 | 域名第17个数字/字母 |  | 0-127
18 | 9745 | 2611 | 域名第18个数字/字母 |  | 0-127
19 | 9746 | 2612 | 域名第19个数字/字母 |  | 0-127
20 | 9747 | 2613 | 域名第20个数字/字母 |  | 0-127
21 | 9748 | 2614 | 域名第21个数字/字母 |  | 0-127
22 | 9749 | 2615 | 域名第22个数字/字母 | 0 | 0-127
23 | 9750 | 2616 | 域名第23个数字/字母 | 0 | 0-127
24 | 9751 | 2617 | 域名第24个数字/字母 | 0 | 0-127
25 | 9752 | 2618 | 域名第25个数字/字母 | 0 | 0-127
26 | 9753 | 2619 | 域名第26个数字/字母 | 0 | 0-127
27 | 9754 | 261A | 域名第27个数字/字母 | 0 | 0-127
28 | 9755 | 261B | 域名第28个数字/字母 | 0 | 0-127
29 | 9756 | 261C | 域名第29个数字/字母 | 0 | 0-127
30 | 9757 | 261D | 域名第30个数字/字母 | 0 | 0-127
31 | 9758 | 261E | 域名第31个数字/字母 | 0 | 0-127
32 | 9759 | 261F | 域名第32个数字/字母 | 0 | 0-127
33 | 9760 | 2620 | 域名第33个数字/字母 | 0 | 0-127
34 | 9761 | 2621 | 域名第34个数字/字母 | 0 | 0-127
35 | 9762 | 2622 | 域名第35个数字/字母 | 0 | 0-127
36 | 9763 | 2623 | 域名第36个数字/字母 | 0 | 0-127
37 | 9764 | 2624 | 域名第37个数字/字母 | 0 | 0-127
38 | 9765 | 2625 | 域名第38个数字/字母 | 0 | 0-127
39 | 9766 | 2626 | 域名第39个数字/字母 | 0 | 0-127
40 | 9767 | 2627 | 域名第40个数字/字母 | 0 | 0-127
41 | 9768 | 2628 | 域名第41个数字/字母 | 0 | 0-127
42 | 9769 | 2629 | 域名第42个数字/字母 | 0 | 0-127
43 | 9770 | 262A | 域名第43个数字/字母 | 0 | 0-127
44 | 9771 | 262B | 域名第44个数字/字母 | 0 | 0-127
45 | 9772 | 262C | 域名第45个数字/字母 | 0 | 0-127
46 | 9773 | 262D | 域名第46个数字/字母 | 0 | 0-127
47 | 9774 | 262E | 域名第47个数字/字母 | 0 | 0-127
48 | 9775 | 262F | 域名第48个数字/字母 | 0 | 0-127
49 | 9776 | 2630 | 域名第49个数字/字母 | 0 | 0-127
50 | 9777 | 2631 | 域名第50个数字/字母 | 0 | 0-127
51 | 9778 | 2632 | 域名第51个数字/字母 | 0 | 0-127
52 | 9779 | 2633 | 域名第52个数字/字母 | 0 | 0-127
53 | 9780 | 2634 | 域名第53个数字/字母 | 0 | 0-127
54 | 9781 | 2635 | 域名第54个数字/字母 | 0 | 0-127
55 | 9782 | 2636 | 域名第55个数字/字母 | 0 | 0-127
56 | 9783 | 2637 | 域名第56个数字/字母 | 0 | 0-127
57 | 9784 | 2638 | 域名第57个数字/字母 | 0 | 0-127
58 | 9785 | 2639 | 域名第58个数字/字母 | 0 | 0-127
59 | 9786 | 263A | 域名第59个数字/字母 | 0 | 0-127
60 | 9787 | 263B | 域名第60个数字/字母 | 0 | 0-127
61 | 9788 | 263C | 域名第61个数字/字母 | 0 | 0-127
62 | 9789 | 263D | 域名第62个数字/字母 | 0 | 0-127
63 | 9790 | 263E | 域名第63个数字/字母 | 0 | 0-127
64 | 9791 | 263F | 域名第64个数字/字母 | 0 | 0-127
65 | 9792 | 2640 | 密第1个数字/字母 | test123 | 0-127
66 | 9793 | 2641 | 密第2个数字/字母 |  | 0-127
67 | 9794 | 2642 | 密第3个数字/字母 |  | 0-127
68 | 9795 | 2643 | 密第4个数字/字母 |  | 0-127
69 | 9796 | 2644 | 密第5个数字/字母 |  | 0-127
70 | 9797 | 2645 | 密第6个数字/字母 |  | 0-127
71 | 9798 | 2646 | 密第7个数字/字母 |  | 0-127
72 | 9799 | 2647 | 密第8个数字/字母 | 0 | 0-127
73 | 9800 | 2648 | 密第9个数字/字母 | 0 | 0-127
74 | 9801 | 2649 | 密第10个数字/字母 | 0 | 0-127
75 | 9802 | 264A | 密第11个数字/字母 | 0 | 0-127
76 | 9803 | 264B | 密第12个数字/字母 | 0 | 0-127
77 | 9804 | 264C | 密第13个数字/字母 | 0 | 0-127
78 | 9805 | 264D | 密第14个数字/字母 | 0 | 0-127
79 | 9806 | 264E | 密第15个数字/字母 | 0 | 0-127
80 | 9807 | 264F | 密第16个数字/字母 | 0 | 0-127
81 | 9808 | 2650 | 密第17个数字/字母 | 0 | 0-127
82 | 9809 | 2651 | 密第18个数字/字母 | 0 | 0-127
83 | 9810 | 2652 | 密第19个数字/字母 | 0 | 0-127
84 | 9811 | 2653 | 密第20个数字/字母 | 0 | 0-127
85 | 9812 | 2654 | 密第21个数字/字母 | 0 | 0-127
86 | 9813 | 2655 | 密第22个数字/字母 | 0 | 0-127
87 | 9814 | 2656 | 密第23个数字/字母 | 0 | 0-127
88 | 9815 | 2657 | 密第24个数字/字母 | 0 | 0-127
89 | 9816 | 2658 | 密第25个数字/字母 | 0 | 0-127
90 | 9817 | 2659 | 密第26个数字/字母 | 0 | 0-127
91 | 9818 | 265A | 密第27个数字/字母 | 0 | 0-127
92 | 9819 | 265B | 密第28个数字/字母 | 0 | 0-127
93 | 9820 | 265C | 密第29个数字/字母 | 0 | 0-127
94 | 9821 | 265D | 密第30个数字/字母 | 0 | 0-127
95 | 9822 | 265E | 密第31个数字/字母 | 0 | 0-127
96 | 9823 | 265F | 密第32个数字/字母 | 0 | 0-127

## 2XXX（Threshold alarm）
Threshold alarm Set(function code 03 read, 06/10 write)
No. | address Decimal | address Hexadecimal | / | Name | Data Type | Default | Range | Unit | Mark
1 | 8704 | 2200 | Slave Sensor No. 1 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
2 | 8705 | 2201 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
3 | 8706 | 2202 | Slave Sensor No. 2 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
4 | 8707 | 2203 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
5 | 8708 | 2204 | Slave Sensor No. 3 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
6 | 8709 | 2205 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
7 | 8710 | 2206 | Slave Sensor No. 4 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
8 | 8711 | 2207 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
9 | 8712 | 2208 | Slave Sensor No. 5 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
10 | 8713 | 2209 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
11 | 8714 | 220A | Slave Sensor No. 6 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
12 | 8715 | 220B |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
13 | 8716 | 220C | Slave Sensor No. 7 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
14 | 8717 | 220D |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
15 | 8718 | 220E | Slave Sensor No. 8 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
16 | 8719 | 220F |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
17 | 8720 | 2210 | Slave Sensor No. 9 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
18 | 8721 | 2211 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
19 | 8722 | 2212 | Slave Sensor No. 10 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
20 | 8723 | 2213 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
21 | 8724 | 2214 | Slave Sensor No. 11 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
22 | 8725 | 2215 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
23 | 8726 | 2216 | Slave Sensor No. 12 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
24 | 8727 | 2217 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
25 | 8728 | 2218 | Slave Sensor No. 13 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
26 | 8729 | 2219 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
27 | 8730 | 221A | Slave Sensor No. 14 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
28 | 8731 | 221B |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
29 | 8732 | 221C | Slave Sensor No. 15 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
30 | 8733 | 221D |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
31 | 8734 | 221E | Slave Sensor No. 16 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
32 | 8735 | 221F |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
33 | 8736 | 2220 | Slave Sensor No. 17 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
34 | 8737 | 2221 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
35 | 8738 | 2222 | Slave Sensor No. 18 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
36 | 8739 | 2223 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
37 | 8740 | 2224 | Slave Sensor No. 19 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
38 | 8741 | 2225 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
39 | 8742 | 2226 | Slave Sensor No. 20 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
40 | 8743 | 2227 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
41 | 8744 | 2228 | Slave Sensor No. 21 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
42 | 8745 | 2229 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
43 | 8746 | 222A | Slave Sensor No. 22 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
44 | 8747 | 222B |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
45 | 8748 | 222C | Slave Sensor No. 23 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
46 | 8749 | 222D |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
47 | 8750 | 222E | Slave Sensor No. 24 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
48 | 8751 | 222F |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
49 | 8752 | 2230 | Slave Sensor No. 25 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
50 | 8753 | 2231 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
51 | 8754 | 2232 | Slave Sensor No. 26 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
52 | 8755 | 2233 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
53 | 8756 | 2234 | Slave Sensor No. 27 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
54 | 8757 | 2235 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
55 | 8758 | 2236 | Slave Sensor No. 28 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
56 | 8759 | 2237 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
57 | 8760 | 2238 | Slave Sensor No. 29 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
58 | 8761 | 2239 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
59 | 8762 | 223A | Slave Sensor No. 30 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
60 | 8763 | 223B |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
61 | 8764 | 223C | Slave Sensor No. 31 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
62 | 8765 | 223D |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
63 | 8766 | 223E | Slave Sensor No. 32 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
64 | 8767 | 223F |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
65 | 8768 | 2240 | Slave Sensor No. 33 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
66 | 8769 | 2241 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
67 | 8770 | 2242 | Slave Sensor No. 34 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
68 | 8771 | 2243 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
69 | 8772 | 2244 | Slave Sensor No. 35 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
70 | 8773 | 2245 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
71 | 8774 | 2246 | Slave Sensor No. 36 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
72 | 8775 | 2247 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
73 | 8776 | 2248 | Slave Sensor No. 37 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
74 | 8777 | 2249 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
75 | 8778 | 224A | Slave Sensor No. 38 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
76 | 8779 | 224B |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
77 | 8780 | 224C | Slave Sensor No. 39 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
78 | 8781 | 224D |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
79 | 8782 | 224E | Slave Sensor No. 40 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
80 | 8783 | 224F |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
81 | 8784 | 2250 | Slave Sensor No. 41 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
82 | 8785 | 2251 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
83 | 8786 | 2252 | Slave Sensor No. 42 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
84 | 8787 | 2253 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
85 | 8788 | 2254 | Slave Sensor No. 43 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
86 | 8789 | 2255 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
87 | 8790 | 2256 | Slave Sensor No. 44 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
88 | 8791 | 2257 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
89 | 8792 | 2258 | Slave Sensor No. 45 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
90 | 8793 | 2259 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
91 | 8794 | 225A | Slave Sensor No. 46 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
92 | 8795 | 225B |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
93 | 8796 | 225C | Slave Sensor No. 47 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
94 | 8797 | 225D |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
95 | 8798 | 225E | Slave Sensor No. 48 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
96 | 8799 | 225F |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
97 | 8800 | 2260 | Slave Sensor No. 49 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
98 | 8801 | 2261 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
99 | 8802 | 2262 | Slave Sensor No. 50 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
100 | 8803 | 2263 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
101 | 8804 | 2264 | Slave Sensor No. 51 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
102 | 8805 | 2265 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
103 | 8806 | 2266 | Slave Sensor No. 52 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
104 | 8807 | 2267 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
105 | 8808 | 2268 | Slave Sensor No. 53 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
106 | 8809 | 2269 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
107 | 8810 | 226A | Slave Sensor No. 54 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
108 | 8811 | 226B |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
109 | 8812 | 226C | Slave Sensor No. 55 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
110 | 8813 | 226D |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
111 | 8814 | 226E | Slave Sensor No. 56 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
112 | 8815 | 226F |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
113 | 8816 | 2270 | Slave Sensor No. 57 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
114 | 8817 | 2271 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
115 | 8818 | 2272 | Slave Sensor No. 58 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
116 | 8819 | 2273 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
117 | 8820 | 2274 | Slave Sensor No. 59 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
118 | 8821 | 2275 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
119 | 8822 | 2276 | Slave Sensor No. 60 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
120 | 8823 | 2277 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
121 | 8824 | 2278 | Slave Sensor No. 61 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
122 | 8825 | 2279 |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
123 | 8826 | 227A | Slave Sensor No. 62 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
124 | 8827 | 227B |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
125 | 8828 | 227C | Slave Sensor No. 63 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
126 | 8829 | 227D |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10
127 | 8830 | 227E | Slave Sensor No. 64 over-limited value setting | set current limited value | Unsigned 16 bit | 50 | 0-65535 | A/10 | *10
128 | 8831 | 227F |  | set temperature limited value | Unsigned 16 bit | 100 | 0-65535 | ℃/10 | *10

## 2XXX（limited value alarm）
Alarm Setting(function code 03 read, 06/10 write
No. | address Decimal | address Hexadecimal |  | Name | Data Type | Default | Range | Unit | Mark
1 | 8960 | 2300 | Slave Sensor No. 1 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
2 | 8961 | 2301 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
3 | 8962 | 2302 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
4 | 8963 | 2303 |  | Reserved |  | 0
5 | 8964 | 2304 | Slave Sensor No. 1 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
6 | 8965 | 2305 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
7 | 8966 | 2306 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
8 | 8967 | 2307 |  | Reserved |  | 0
9 | 8968 | 2308 | Slave Sensor No. 1 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
10 | 8969 | 2309 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
11 | 8970 | 230A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
12 | 8971 | 230B |  | Reserved |  | 0
13 | 8972 | 230C | Slave Sensor No. 1 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
14 | 8973 | 230D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
15 | 8974 | 230E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
16 | 8975 | 230F |  | Reserved |  | 0
17 | 8976 | 2310 | Slave Sensor No. 2 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
18 | 8977 | 2311 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
19 | 8978 | 2312 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
20 | 8979 | 2313 |  | Reserved |  | 0
21 | 8980 | 2314 | Slave Sensor No. 2 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
22 | 8981 | 2315 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
23 | 8982 | 2316 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
24 | 8983 | 2317 |  | Reserved |  | 0
25 | 8984 | 2318 | Slave Sensor No. 2 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
26 | 8985 | 2319 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
27 | 8986 | 231A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
28 | 8987 | 231B |  | Reserved |  | 0
29 | 8988 | 231C | Slave Sensor No. 2 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
30 | 8989 | 231D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
31 | 8990 | 231E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
32 | 8991 | 231F |  | Reserved |  | 0
33 | 8992 | 2320 | Slave Sensor No. 3 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
34 | 8993 | 2321 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
35 | 8994 | 2322 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
36 | 8995 | 2323 |  | Reserved |  | 0
37 | 8996 | 2324 | Slave Sensor No. 3 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
38 | 8997 | 2325 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
39 | 8998 | 2326 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
40 | 8999 | 2327 |  | Reserved |  | 0
41 | 9000 | 2328 | Slave Sensor No. 3 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
42 | 9001 | 2329 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
43 | 9002 | 232A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
44 | 9003 | 232B |  | Reserved |  | 0
45 | 9004 | 232C | Slave Sensor No. 3 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
46 | 9005 | 232D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
47 | 9006 | 232E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
48 | 9007 | 232F |  | Reserved |  | 0
49 | 9008 | 2330 | Slave Sensor No. 4 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
50 | 9009 | 2331 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
51 | 9010 | 2332 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
52 | 9011 | 2333 |  | Reserved |  | 0
53 | 9012 | 2334 | Slave Sensor No. 4 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
54 | 9013 | 2335 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
55 | 9014 | 2336 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
56 | 9015 | 2337 |  | Reserved |  | 0
57 | 9016 | 2338 | Slave Sensor No. 4 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
58 | 9017 | 2339 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
59 | 9018 | 233A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
60 | 9019 | 233B |  | Reserved |  | 0
61 | 9020 | 233C | Slave Sensor No. 4 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
62 | 9021 | 233D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
63 | 9022 | 233E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
64 | 9023 | 233F |  | Reserved |  | 0
65 | 9024 | 2340 | Slave Sensor No. 5 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
66 | 9025 | 2341 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
67 | 9026 | 2342 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
68 | 9027 | 2343 |  | Reserved |  | 0
69 | 9028 | 2344 | Slave Sensor No. 5 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
70 | 9029 | 2345 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
71 | 9030 | 2346 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
72 | 9031 | 2347 |  | Reserved |  | 0
73 | 9032 | 2348 | Slave Sensor No. 5 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
74 | 9033 | 2349 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
75 | 9034 | 234A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
76 | 9035 | 234B |  | Reserved |  | 0
77 | 9036 | 234C | Slave Sensor No. 5 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
78 | 9037 | 234D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
79 | 9038 | 234E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
80 | 9039 | 234F |  | Reserved |  | 0
81 | 9040 | 2350 | Slave Sensor No. 6 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
82 | 9041 | 2351 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
83 | 9042 | 2352 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
84 | 9043 | 2353 |  | Reserved |  | 0
85 | 9044 | 2354 | Slave Sensor No. 6 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
86 | 9045 | 2355 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
87 | 9046 | 2356 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
88 | 9047 | 2357 |  | Reserved |  | 0
89 | 9048 | 2358 | Slave Sensor No. 6 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
90 | 9049 | 2359 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
91 | 9050 | 235A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
92 | 9051 | 235B |  | Reserved |  | 0
93 | 9052 | 235C | Slave Sensor No. 6 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
94 | 9053 | 235D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
95 | 9054 | 235E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
96 | 9055 | 235F |  | Reserved |  | 0
97 | 9056 | 2360 | Slave Sensor No. 7 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
98 | 9057 | 2361 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
99 | 9058 | 2362 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
100 | 9059 | 2363 |  | Reserved |  | 0
101 | 9060 | 2364 | Slave Sensor No. 7 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
102 | 9061 | 2365 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
103 | 9062 | 2366 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
104 | 9063 | 2367 |  | Reserved |  | 0
105 | 9064 | 2368 | Slave Sensor No. 7 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
106 | 9065 | 2369 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
107 | 9066 | 236A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
108 | 9067 | 236B |  | Reserved |  | 0
109 | 9068 | 236C | Slave Sensor No. 7 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
110 | 9069 | 236D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
111 | 9070 | 236E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
112 | 9071 | 236F |  | Reserved |  | 0
113 | 9072 | 2370 | Slave Sensor No. 8 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
114 | 9073 | 2371 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
115 | 9074 | 2372 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
116 | 9075 | 2373 |  | Reserved |  | 0
117 | 9076 | 2374 | Slave Sensor No. 8 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
118 | 9077 | 2375 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
119 | 9078 | 2376 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
120 | 9079 | 2377 |  | Reserved |  | 0
121 | 9080 | 2378 | Slave Sensor No. 8 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
122 | 9081 | 2379 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
123 | 9082 | 237A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
124 | 9083 | 237B |  | Reserved |  | 0
125 | 9084 | 237C | Slave Sensor No. 8 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
126 | 9085 | 237D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
127 | 9086 | 237E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
128 | 9087 | 237F |  | Reserved |  | 0
129 | 9088 | 2380 | Slave Sensor No. 9 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
130 | 9089 | 2381 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
131 | 9090 | 2382 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
132 | 9091 | 2383 |  | Reserved |  | 0
133 | 9092 | 2384 | Slave Sensor No. 9 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
134 | 9093 | 2385 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
135 | 9094 | 2386 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
136 | 9095 | 2387 |  | Reserved |  | 0
137 | 9096 | 2388 | Slave Sensor No. 9 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
138 | 9097 | 2389 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
139 | 9098 | 238A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
140 | 9099 | 238B |  | Reserved |  | 0
141 | 9100 | 238C | Slave Sensor No. 9 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
142 | 9101 | 238D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
143 | 9102 | 238E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
144 | 9103 | 238F |  | Reserved |  | 0
145 | 9104 | 2390 | Slave Sensor No. 10 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
146 | 9105 | 2391 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
147 | 9106 | 2392 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
148 | 9107 | 2393 |  | Reserved |  | 0
149 | 9108 | 2394 | Slave Sensor No. 10 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
150 | 9109 | 2395 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
151 | 9110 | 2396 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
152 | 9111 | 2397 |  | Reserved |  | 0
153 | 9112 | 2398 | Slave Sensor No. 10 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
154 | 9113 | 2399 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
155 | 9114 | 239A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
156 | 9115 | 239B |  | Reserved |  | 0
157 | 9116 | 239C | Slave Sensor No. 10 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
158 | 9117 | 239D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
159 | 9118 | 239E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
160 | 9119 | 239F |  | Reserved |  | 0
161 | 9120 | 23A0 | Slave Sensor No. 11 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
162 | 9121 | 23A1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
163 | 9122 | 23A2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
164 | 9123 | 23A3 |  | Reserved |  | 0
165 | 9124 | 23A4 | Slave Sensor No. 11 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
166 | 9125 | 23A5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
167 | 9126 | 23A6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
168 | 9127 | 23A7 |  | Reserved |  | 0
169 | 9128 | 23A8 | Slave Sensor No. 11 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
170 | 9129 | 23A9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
171 | 9130 | 23AA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
172 | 9131 | 23AB |  | Reserved |  | 0
173 | 9132 | 23AC | Slave Sensor No. 11 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
174 | 9133 | 23AD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
175 | 9134 | 23AE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
176 | 9135 | 23AF |  | Reserved |  | 0
177 | 9136 | 23B0 | Slave Sensor No. 12 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
178 | 9137 | 23B1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
179 | 9138 | 23B2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
180 | 9139 | 23B3 |  | Reserved |  | 0
181 | 9140 | 23B4 | Slave Sensor No. 12 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
182 | 9141 | 23B5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
183 | 9142 | 23B6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
184 | 9143 | 23B7 |  | Reserved |  | 0
185 | 9144 | 23B8 | Slave Sensor No. 12 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
186 | 9145 | 23B9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
187 | 9146 | 23BA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
188 | 9147 | 23BB |  | Reserved |  | 0
189 | 9148 | 23BC | Slave Sensor No. 12 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
190 | 9149 | 23BD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
191 | 9150 | 23BE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
192 | 9151 | 23BF |  | Reserved |  | 0
193 | 9152 | 23C0 | Slave Sensor No. 13 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
194 | 9153 | 23C1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
195 | 9154 | 23C2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
196 | 9155 | 23C3 |  | Reserved |  | 0
197 | 9156 | 23C4 | Slave Sensor No. 13 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
198 | 9157 | 23C5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
199 | 9158 | 23C6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
200 | 9159 | 23C7 |  | Reserved |  | 0
201 | 9160 | 23C8 | Slave Sensor No. 13 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
202 | 9161 | 23C9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
203 | 9162 | 23CA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
204 | 9163 | 23CB |  | Reserved |  | 0
205 | 9164 | 23CC | Slave Sensor No. 13 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
206 | 9165 | 23CD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
207 | 9166 | 23CE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
208 | 9167 | 23CF |  | Reserved |  | 0
209 | 9168 | 23D0 | Slave Sensor No. 14 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
210 | 9169 | 23D1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
211 | 9170 | 23D2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
212 | 9171 | 23D3 |  | Reserved |  | 0
213 | 9172 | 23D4 | Slave Sensor No. 14 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
214 | 9173 | 23D5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
215 | 9174 | 23D6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
216 | 9175 | 23D7 |  | Reserved |  | 0
217 | 9176 | 23D8 | Slave Sensor No. 14 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
218 | 9177 | 23D9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
219 | 9178 | 23DA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
220 | 9179 | 23DB |  | Reserved |  | 0
221 | 9180 | 23DC | Slave Sensor No. 14 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
222 | 9181 | 23DD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
223 | 9182 | 23DE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
224 | 9183 | 23DF |  | Reserved |  | 0
225 | 9184 | 23E0 | Slave Sensor No. 15 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
226 | 9185 | 23E1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
227 | 9186 | 23E2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
228 | 9187 | 23E3 |  | Reserved |  | 0
229 | 9188 | 23E4 | Slave Sensor No. 15 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
230 | 9189 | 23E5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
231 | 9190 | 23E6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
232 | 9191 | 23E7 |  | Reserved |  | 0
233 | 9192 | 23E8 | Slave Sensor No. 15 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
234 | 9193 | 23E9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
235 | 9194 | 23EA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
236 | 9195 | 23EB |  | Reserved |  | 0
237 | 9196 | 23EC | Slave Sensor No. 15 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
238 | 9197 | 23ED |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
239 | 9198 | 23EE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
240 | 9199 | 23EF |  | Reserved |  | 0
241 | 9200 | 23F0 | Slave Sensor No. 16 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
242 | 9201 | 23F1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
243 | 9202 | 23F2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
244 | 9203 | 23F3 |  | Reserved |  | 0
245 | 9204 | 23F4 | Slave Sensor No. 16 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
246 | 9205 | 23F5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
247 | 9206 | 23F6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
248 | 9207 | 23F7 |  | Reserved |  | 0
249 | 9208 | 23F8 | Slave Sensor No. 16 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
250 | 9209 | 23F9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
251 | 9210 | 23FA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
252 | 9211 | 23FB |  | Reserved |  | 0
253 | 9212 | 23FC | Slave Sensor No. 16 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
254 | 9213 | 23FD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
255 | 9214 | 23FE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
256 | 9215 | 23FF |  | Reserved |  | 0
257 | 9216 | 2400 | Slave Sensor No. 17 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
258 | 9217 | 2401 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
259 | 9218 | 2402 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
260 | 9219 | 2403 |  | Reserved |  | 0
261 | 9220 | 2404 | Slave Sensor No. 17 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
262 | 9221 | 2405 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
263 | 9222 | 2406 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
264 | 9223 | 2407 |  | Reserved |  | 0
265 | 9224 | 2408 | Slave Sensor No. 17 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
266 | 9225 | 2409 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
267 | 9226 | 240A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
268 | 9227 | 240B |  | Reserved |  | 0
269 | 9228 | 240C | Slave Sensor No. 17 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
270 | 9229 | 240D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
271 | 9230 | 240E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
272 | 9231 | 240F |  | Reserved |  | 0
273 | 9232 | 2410 | Slave Sensor No. 18 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
274 | 9233 | 2411 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
275 | 9234 | 2412 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
276 | 9235 | 2413 |  | Reserved |  | 0
277 | 9236 | 2414 | Slave Sensor No. 18 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
278 | 9237 | 2415 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
279 | 9238 | 2416 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
280 | 9239 | 2417 |  | Reserved |  | 0
281 | 9240 | 2418 | Slave Sensor No. 18 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
282 | 9241 | 2419 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
283 | 9242 | 241A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
284 | 9243 | 241B |  | Reserved |  | 0
285 | 9244 | 241C | Slave Sensor No. 18 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
286 | 9245 | 241D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
287 | 9246 | 241E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
288 | 9247 | 241F |  | Reserved |  | 0
289 | 9248 | 2420 | Slave Sensor No. 19 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
290 | 9249 | 2421 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
291 | 9250 | 2422 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
292 | 9251 | 2423 |  | Reserved |  | 0
293 | 9252 | 2424 | Slave Sensor No. 19 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
294 | 9253 | 2425 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
295 | 9254 | 2426 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
296 | 9255 | 2427 |  | Reserved |  | 0
297 | 9256 | 2428 | Slave Sensor No. 19 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
298 | 9257 | 2429 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
299 | 9258 | 242A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
300 | 9259 | 242B |  | Reserved |  | 0
301 | 9260 | 242C | Slave Sensor No. 19 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
302 | 9261 | 242D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
303 | 9262 | 242E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
304 | 9263 | 242F |  | Reserved |  | 0
305 | 9264 | 2430 | Slave Sensor No. 20 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
306 | 9265 | 2431 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
307 | 9266 | 2432 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
308 | 9267 | 2433 |  | Reserved |  | 0
309 | 9268 | 2434 | Slave Sensor No. 20 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
310 | 9269 | 2435 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
311 | 9270 | 2436 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
312 | 9271 | 2437 |  | Reserved |  | 0
313 | 9272 | 2438 | Slave Sensor No. 20 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
314 | 9273 | 2439 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
315 | 9274 | 243A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
316 | 9275 | 243B |  | Reserved |  | 0
317 | 9276 | 243C | Slave Sensor No. 20 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
318 | 9277 | 243D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
319 | 9278 | 243E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
320 | 9279 | 243F |  | Reserved |  | 0
321 | 9280 | 2440 | Slave Sensor No. 21 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
322 | 9281 | 2441 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
323 | 9282 | 2442 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
324 | 9283 | 2443 |  | Reserved |  | 0
325 | 9284 | 2444 | Slave Sensor No. 21 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
326 | 9285 | 2445 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
327 | 9286 | 2446 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
328 | 9287 | 2447 |  | Reserved |  | 0
329 | 9288 | 2448 | Slave Sensor No. 21 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
330 | 9289 | 2449 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
331 | 9290 | 244A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
332 | 9291 | 244B |  | Reserved |  | 0
333 | 9292 | 244C | Slave Sensor No. 21 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
334 | 9293 | 244D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
335 | 9294 | 244E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
336 | 9295 | 244F |  | Reserved |  | 0
337 | 9296 | 2450 | Slave Sensor No. 22 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
338 | 9297 | 2451 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
339 | 9298 | 2452 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
340 | 9299 | 2453 |  | Reserved |  | 0
341 | 9300 | 2454 | Slave Sensor No. 22 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
342 | 9301 | 2455 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
343 | 9302 | 2456 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
344 | 9303 | 2457 |  | Reserved |  | 0
345 | 9304 | 2458 | Slave Sensor No. 22 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
346 | 9305 | 2459 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
347 | 9306 | 245A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
348 | 9307 | 245B |  | Reserved |  | 0
349 | 9308 | 245C | Slave Sensor No. 22 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
350 | 9309 | 245D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
351 | 9310 | 245E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
352 | 9311 | 245F |  | Reserved |  | 0
353 | 9312 | 2460 | Slave Sensor No. 23 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
354 | 9313 | 2461 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
355 | 9314 | 2462 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
356 | 9315 | 2463 |  | Reserved |  | 0
357 | 9316 | 2464 | Slave Sensor No. 23 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
358 | 9317 | 2465 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
359 | 9318 | 2466 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
360 | 9319 | 2467 |  | Reserved |  | 0
361 | 9320 | 2468 | Slave Sensor No. 23 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
362 | 9321 | 2469 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
363 | 9322 | 246A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
364 | 9323 | 246B |  | Reserved |  | 0
365 | 9324 | 246C | Slave Sensor No. 23 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
366 | 9325 | 246D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
367 | 9326 | 246E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
368 | 9327 | 246F |  | Reserved |  | 0
369 | 9328 | 2470 | Slave Sensor No. 24 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
370 | 9329 | 2471 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
371 | 9330 | 2472 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
372 | 9331 | 2473 |  | Reserved |  | 0
373 | 9332 | 2474 | Slave Sensor No. 24 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
374 | 9333 | 2475 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
375 | 9334 | 2476 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
376 | 9335 | 2477 |  | Reserved |  | 0
377 | 9336 | 2478 | Slave Sensor No. 24 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
378 | 9337 | 2479 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
379 | 9338 | 247A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
380 | 9339 | 247B |  | Reserved |  | 0
381 | 9340 | 247C | Slave Sensor No. 24 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
382 | 9341 | 247D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
383 | 9342 | 247E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
384 | 9343 | 247F |  | Reserved |  | 0
385 | 9344 | 2480 | Slave Sensor No. 25 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
386 | 9345 | 2481 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
387 | 9346 | 2482 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
388 | 9347 | 2483 |  | Reserved |  | 0
389 | 9348 | 2484 | Slave Sensor No. 25 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
390 | 9349 | 2485 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
391 | 9350 | 2486 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
392 | 9351 | 2487 |  | Reserved |  | 0
393 | 9352 | 2488 | Slave Sensor No. 25 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
394 | 9353 | 2489 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
395 | 9354 | 248A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
396 | 9355 | 248B |  | Reserved |  | 0
397 | 9356 | 248C | Slave Sensor No. 25 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
398 | 9357 | 248D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
399 | 9358 | 248E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
400 | 9359 | 248F |  | Reserved |  | 0
401 | 9360 | 2490 | Slave Sensor No. 26 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
402 | 9361 | 2491 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
403 | 9362 | 2492 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
404 | 9363 | 2493 |  | Reserved |  | 0
405 | 9364 | 2494 | Slave Sensor No. 26 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
406 | 9365 | 2495 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
407 | 9366 | 2496 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
408 | 9367 | 2497 |  | Reserved |  | 0
409 | 9368 | 2498 | Slave Sensor No. 26 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
410 | 9369 | 2499 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
411 | 9370 | 249A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
412 | 9371 | 249B |  | Reserved |  | 0
413 | 9372 | 249C | Slave Sensor No. 26 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
414 | 9373 | 249D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
415 | 9374 | 249E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
416 | 9375 | 249F |  | Reserved |  | 0
417 | 9376 | 24A0 | Slave Sensor No. 27 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
418 | 9377 | 24A1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
419 | 9378 | 24A2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
420 | 9379 | 24A3 |  | Reserved |  | 0
421 | 9380 | 24A4 | Slave Sensor No. 27 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
422 | 9381 | 24A5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
423 | 9382 | 24A6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
424 | 9383 | 24A7 |  | Reserved |  | 0
425 | 9384 | 24A8 | Slave Sensor No. 27 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
426 | 9385 | 24A9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
427 | 9386 | 24AA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
428 | 9387 | 24AB |  | Reserved |  | 0
429 | 9388 | 24AC | Slave Sensor No. 27 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
430 | 9389 | 24AD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
431 | 9390 | 24AE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
432 | 9391 | 24AF |  | Reserved |  | 0
433 | 9392 | 24B0 | Slave Sensor No. 28 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
434 | 9393 | 24B1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
435 | 9394 | 24B2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
436 | 9395 | 24B3 |  | Reserved |  | 0
437 | 9396 | 24B4 | Slave Sensor No. 28 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
438 | 9397 | 24B5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
439 | 9398 | 24B6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
440 | 9399 | 24B7 |  | Reserved |  | 0
441 | 9400 | 24B8 | Slave Sensor No. 28 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
442 | 9401 | 24B9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
443 | 9402 | 24BA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
444 | 9403 | 24BB |  | Reserved |  | 0
445 | 9404 | 24BC | Slave Sensor No. 28 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
446 | 9405 | 24BD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
447 | 9406 | 24BE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
448 | 9407 | 24BF |  | Reserved |  | 0
449 | 9408 | 24C0 | Slave Sensor No. 29 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
450 | 9409 | 24C1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
451 | 9410 | 24C2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
452 | 9411 | 24C3 |  | Reserved |  | 0
453 | 9412 | 24C4 | Slave Sensor No. 29 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
454 | 9413 | 24C5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
455 | 9414 | 24C6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
456 | 9415 | 24C7 |  | Reserved |  | 0
457 | 9416 | 24C8 | Slave Sensor No. 29 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
458 | 9417 | 24C9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
459 | 9418 | 24CA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
460 | 9419 | 24CB |  | Reserved |  | 0
461 | 9420 | 24CC | Slave Sensor No. 29 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
462 | 9421 | 24CD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
463 | 9422 | 24CE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
464 | 9423 | 24CF |  | Reserved |  | 0
465 | 9424 | 24D0 | Slave Sensor No. 30 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
466 | 9425 | 24D1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
467 | 9426 | 24D2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
468 | 9427 | 24D3 |  | Reserved |  | 0
469 | 9428 | 24D4 | Slave Sensor No. 30 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
470 | 9429 | 24D5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
471 | 9430 | 24D6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
472 | 9431 | 24D7 |  | Reserved |  | 0
473 | 9432 | 24D8 | Slave Sensor No. 30 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
474 | 9433 | 24D9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
475 | 9434 | 24DA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
476 | 9435 | 24DB |  | Reserved |  | 0
477 | 9436 | 24DC | Slave Sensor No. 30 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
478 | 9437 | 24DD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
479 | 9438 | 24DE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
480 | 9439 | 24DF |  | Reserved |  | 0
481 | 9440 | 24E0 | Slave Sensor No. 31 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
482 | 9441 | 24E1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
483 | 9442 | 24E2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
484 | 9443 | 24E3 |  | Reserved |  | 0
485 | 9444 | 24E4 | Slave Sensor No. 31 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
486 | 9445 | 24E5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
487 | 9446 | 24E6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
488 | 9447 | 24E7 |  | Reserved |  | 0
489 | 9448 | 24E8 | Slave Sensor No. 31 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
490 | 9449 | 24E9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
491 | 9450 | 24EA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
492 | 9451 | 24EB |  | Reserved |  | 0
493 | 9452 | 24EC | Slave Sensor No. 31 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
494 | 9453 | 24ED |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
495 | 9454 | 24EE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
496 | 9455 | 24EF |  | Reserved |  | 0
497 | 9456 | 24F0 | Slave Sensor No. 32 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
498 | 9457 | 24F1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
499 | 9458 | 24F2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
500 | 9459 | 24F3 |  | Reserved |  | 0
501 | 9460 | 24F4 | Slave Sensor No. 32 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
502 | 9461 | 24F5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
503 | 9462 | 24F6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
504 | 9463 | 24F7 |  | Reserved |  | 0
505 | 9464 | 24F8 | Slave Sensor No. 32 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
506 | 9465 | 24F9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
507 | 9466 | 24FA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
508 | 9467 | 24FB |  | Reserved |  | 0
509 | 9468 | 24FC | Slave Sensor No. 32 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
510 | 9469 | 24FD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
511 | 9470 | 24FE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
512 | 9471 | 24FF |  | Reserved |  | 0
513 | 9472 | 2500 | Slave Sensor No. 33 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
514 | 9473 | 2501 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
515 | 9474 | 2502 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
516 | 9475 | 2503 |  | Reserved |  | 0
517 | 9476 | 2504 | Slave Sensor No. 33 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
518 | 9477 | 2505 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
519 | 9478 | 2506 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
520 | 9479 | 2507 |  | Reserved |  | 0
521 | 9480 | 2508 | Slave Sensor No. 33 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
522 | 9481 | 2509 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
523 | 9482 | 250A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
524 | 9483 | 250B |  | Reserved |  | 0
525 | 9484 | 250C | Slave Sensor No. 33 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
526 | 9485 | 250D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
527 | 9486 | 250E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
528 | 9487 | 250F |  | Reserved |  | 0
529 | 9488 | 2510 | Slave Sensor No. 34 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
530 | 9489 | 2511 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
531 | 9490 | 2512 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
532 | 9491 | 2513 |  | Reserved |  | 0
533 | 9492 | 2514 | Slave Sensor No. 34 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
534 | 9493 | 2515 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
535 | 9494 | 2516 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
536 | 9495 | 2517 |  | Reserved |  | 0
537 | 9496 | 2518 | Slave Sensor No. 34 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
538 | 9497 | 2519 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
539 | 9498 | 251A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
540 | 9499 | 251B |  | Reserved |  | 0
541 | 9500 | 251C | Slave Sensor No. 34 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
542 | 9501 | 251D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
543 | 9502 | 251E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
544 | 9503 | 251F |  | Reserved |  | 0
545 | 9504 | 2520 | Slave Sensor No. 35 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
546 | 9505 | 2521 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
547 | 9506 | 2522 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
548 | 9507 | 2523 |  | Reserved |  | 0
549 | 9508 | 2524 | Slave Sensor No. 35 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
550 | 9509 | 2525 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
551 | 9510 | 2526 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
552 | 9511 | 2527 |  | Reserved |  | 0
553 | 9512 | 2528 | Slave Sensor No. 35 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
554 | 9513 | 2529 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
555 | 9514 | 252A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
556 | 9515 | 252B |  | Reserved |  | 0
557 | 9516 | 252C | Slave Sensor No. 35 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
558 | 9517 | 252D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
559 | 9518 | 252E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
560 | 9519 | 252F |  | Reserved |  | 0
561 | 9520 | 2530 | Slave Sensor No. 36 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
562 | 9521 | 2531 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
563 | 9522 | 2532 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
564 | 9523 | 2533 |  | Reserved |  | 0
565 | 9524 | 2534 | Slave Sensor No. 36 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
566 | 9525 | 2535 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
567 | 9526 | 2536 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
568 | 9527 | 2537 |  | Reserved |  | 0
569 | 9528 | 2538 | Slave Sensor No. 36 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
570 | 9529 | 2539 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
571 | 9530 | 253A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
572 | 9531 | 253B |  | Reserved |  | 0
573 | 9532 | 253C | Slave Sensor No. 36 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
574 | 9533 | 253D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
575 | 9534 | 253E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
576 | 9535 | 253F |  | Reserved |  | 0
577 | 9536 | 2540 | Slave Sensor No. 37 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
578 | 9537 | 2541 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
579 | 9538 | 2542 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
580 | 9539 | 2543 |  | Reserved |  | 0
581 | 9540 | 2544 | Slave Sensor No. 37 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
582 | 9541 | 2545 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
583 | 9542 | 2546 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
584 | 9543 | 2547 |  | Reserved |  | 0
585 | 9544 | 2548 | Slave Sensor No. 37 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
586 | 9545 | 2549 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
587 | 9546 | 254A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
588 | 9547 | 254B |  | Reserved |  | 0
589 | 9548 | 254C | Slave Sensor No. 37 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
590 | 9549 | 254D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
591 | 9550 | 254E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
592 | 9551 | 254F |  | Reserved |  | 0
593 | 9552 | 2550 | Slave Sensor No. 38 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
594 | 9553 | 2551 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
595 | 9554 | 2552 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
596 | 9555 | 2553 |  | Reserved |  | 0
597 | 9556 | 2554 | Slave Sensor No. 38 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
598 | 9557 | 2555 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
599 | 9558 | 2556 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
600 | 9559 | 2557 |  | Reserved |  | 0
601 | 9560 | 2558 | Slave Sensor No. 38 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
602 | 9561 | 2559 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
603 | 9562 | 255A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
604 | 9563 | 255B |  | Reserved |  | 0
605 | 9564 | 255C | Slave Sensor No. 38 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
606 | 9565 | 255D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
607 | 9566 | 255E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
608 | 9567 | 255F |  | Reserved |  | 0
609 | 9568 | 2560 | Slave Sensor No. 39 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
610 | 9569 | 2561 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
611 | 9570 | 2562 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
612 | 9571 | 2563 |  | Reserved |  | 0
613 | 9572 | 2564 | Slave Sensor No. 39 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
614 | 9573 | 2565 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
615 | 9574 | 2566 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
616 | 9575 | 2567 |  | Reserved |  | 0
617 | 9576 | 2568 | Slave Sensor No. 39 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
618 | 9577 | 2569 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
619 | 9578 | 256A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
620 | 9579 | 256B |  | Reserved |  | 0
621 | 9580 | 256C | Slave Sensor No. 39 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
622 | 9581 | 256D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
623 | 9582 | 256E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
624 | 9583 | 256F |  | Reserved |  | 0
625 | 9584 | 2570 | Slave Sensor No. 40 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
626 | 9585 | 2571 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
627 | 9586 | 2572 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
628 | 9587 | 2573 |  | Reserved |  | 0
629 | 9588 | 2574 | Slave Sensor No. 40 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
630 | 9589 | 2575 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
631 | 9590 | 2576 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
632 | 9591 | 2577 |  | Reserved |  | 0
633 | 9592 | 2578 | Slave Sensor No. 40 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
634 | 9593 | 2579 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
635 | 9594 | 257A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
636 | 9595 | 257B |  | Reserved |  | 0
637 | 9596 | 257C | Slave Sensor No. 40 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
638 | 9597 | 257D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
639 | 9598 | 257E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
640 | 9599 | 257F |  | Reserved |  | 0
641 | 9600 | 2580 | Slave Sensor No. 41 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
642 | 9601 | 2581 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
643 | 9602 | 2582 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
644 | 9603 | 2583 |  | Reserved |  | 0
645 | 9604 | 2584 | Slave Sensor No. 41 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
646 | 9605 | 2585 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
647 | 9606 | 2586 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
648 | 9607 | 2587 |  | Reserved |  | 0
649 | 9608 | 2588 | Slave Sensor No. 41 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
650 | 9609 | 2589 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
651 | 9610 | 258A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
652 | 9611 | 258B |  | Reserved |  | 0
653 | 9612 | 258C | Slave Sensor No. 41 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
654 | 9613 | 258D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
655 | 9614 | 258E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
656 | 9615 | 258F |  | Reserved |  | 0
657 | 9616 | 2590 | Slave Sensor No. 42 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
658 | 9617 | 2591 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
659 | 9618 | 2592 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
660 | 9619 | 2593 |  | Reserved |  | 0
661 | 9620 | 2594 | Slave Sensor No. 42 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
662 | 9621 | 2595 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
663 | 9622 | 2596 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
664 | 9623 | 2597 |  | Reserved |  | 0
665 | 9624 | 2598 | Slave Sensor No. 42 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
666 | 9625 | 2599 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
667 | 9626 | 259A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
668 | 9627 | 259B |  | Reserved |  | 0
669 | 9628 | 259C | Slave Sensor No. 42 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
670 | 9629 | 259D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
671 | 9630 | 259E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
672 | 9631 | 259F |  | Reserved |  | 0
673 | 9632 | 25A0 | Slave Sensor No. 43 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
674 | 9633 | 25A1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
675 | 9634 | 25A2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
676 | 9635 | 25A3 |  | Reserved |  | 0
677 | 9636 | 25A4 | Slave Sensor No. 43 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
678 | 9637 | 25A5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
679 | 9638 | 25A6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
680 | 9639 | 25A7 |  | Reserved |  | 0
681 | 9640 | 25A8 | Slave Sensor No. 43 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
682 | 9641 | 25A9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
683 | 9642 | 25AA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
684 | 9643 | 25AB |  | Reserved |  | 0
685 | 9644 | 25AC | Slave Sensor No. 43 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
686 | 9645 | 25AD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
687 | 9646 | 25AE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
688 | 9647 | 25AF |  | Reserved |  | 0
689 | 9648 | 25B0 | Slave Sensor No. 44 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
690 | 9649 | 25B1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
691 | 9650 | 25B2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
692 | 9651 | 25B3 |  | Reserved |  | 0
693 | 9652 | 25B4 | Slave Sensor No. 44 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
694 | 9653 | 25B5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
695 | 9654 | 25B6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
696 | 9655 | 25B7 |  | Reserved |  | 0
697 | 9656 | 25B8 | Slave Sensor No. 44 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
698 | 9657 | 25B9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
699 | 9658 | 25BA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
700 | 9659 | 25BB |  | Reserved |  | 0
701 | 9660 | 25BC | Slave Sensor No. 44 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
702 | 9661 | 25BD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
703 | 9662 | 25BE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
704 | 9663 | 25BF |  | Reserved |  | 0
705 | 9664 | 25C0 | Slave Sensor No. 45 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
706 | 9665 | 25C1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
707 | 9666 | 25C2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
708 | 9667 | 25C3 |  | Reserved |  | 0
709 | 9668 | 25C4 | Slave Sensor No. 45 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
710 | 9669 | 25C5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
711 | 9670 | 25C6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
712 | 9671 | 25C7 |  | Reserved |  | 0
713 | 9672 | 25C8 | Slave Sensor No. 45 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
714 | 9673 | 25C9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
715 | 9674 | 25CA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
716 | 9675 | 25CB |  | Reserved |  | 0
717 | 9676 | 25CC | Slave Sensor No. 45 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
718 | 9677 | 25CD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
719 | 9678 | 25CE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
720 | 9679 | 25CF |  | Reserved |  | 0
721 | 9680 | 25D0 | Slave Sensor No. 46 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
722 | 9681 | 25D1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
723 | 9682 | 25D2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
724 | 9683 | 25D3 |  | Reserved |  | 0
725 | 9684 | 25D4 | Slave Sensor No. 46 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
726 | 9685 | 25D5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
727 | 9686 | 25D6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
728 | 9687 | 25D7 |  | Reserved |  | 0
729 | 9688 | 25D8 | Slave Sensor No. 46 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
730 | 9689 | 25D9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
731 | 9690 | 25DA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
732 | 9691 | 25DB |  | Reserved |  | 0
733 | 9692 | 25DC | Slave Sensor No. 46 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
734 | 9693 | 25DD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
735 | 9694 | 25DE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
736 | 9695 | 25DF |  | Reserved |  | 0
737 | 9696 | 25E0 | Slave Sensor No. 47 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
738 | 9697 | 25E1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
739 | 9698 | 25E2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
740 | 9699 | 25E3 |  | Reserved |  | 0
741 | 9700 | 25E4 | Slave Sensor No. 47 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
742 | 9701 | 25E5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
743 | 9702 | 25E6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
744 | 9703 | 25E7 |  | Reserved |  | 0
745 | 9704 | 25E8 | Slave Sensor No. 47 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
746 | 9705 | 25E9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
747 | 9706 | 25EA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
748 | 9707 | 25EB |  | Reserved |  | 0
749 | 9708 | 25EC | Slave Sensor No. 47 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
750 | 9709 | 25ED |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
751 | 9710 | 25EE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
752 | 9711 | 25EF |  | Reserved |  | 0
753 | 9712 | 25F0 | Slave Sensor No. 48 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
754 | 9713 | 25F1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
755 | 9714 | 25F2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
756 | 9715 | 25F3 |  | Reserved |  | 0
757 | 9716 | 25F4 | Slave Sensor No. 48 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
758 | 9717 | 25F5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
759 | 9718 | 25F6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
760 | 9719 | 25F7 |  | Reserved |  | 0
761 | 9720 | 25F8 | Slave Sensor No. 48 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
762 | 9721 | 25F9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
763 | 9722 | 25FA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
764 | 9723 | 25FB |  | Reserved |  | 0
765 | 9724 | 25FC | Slave Sensor No. 48 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
766 | 9725 | 25FD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
767 | 9726 | 25FE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
768 | 9727 | 25FF |  | Reserved |  | 0
769 | 9728 | 2600 | Slave Sensor No. 49 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
770 | 9729 | 2601 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
771 | 9730 | 2602 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
772 | 9731 | 2603 |  | Reserved |  | 0
773 | 9732 | 2604 | Slave Sensor No. 49 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
774 | 9733 | 2605 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
775 | 9734 | 2606 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
776 | 9735 | 2607 |  | Reserved |  | 0
777 | 9736 | 2608 | Slave Sensor No. 49 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
778 | 9737 | 2609 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
779 | 9738 | 260A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
780 | 9739 | 260B |  | Reserved |  | 0
781 | 9740 | 260C | Slave Sensor No. 49 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
782 | 9741 | 260D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
783 | 9742 | 260E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
784 | 9743 | 260F |  | Reserved |  | 0
785 | 9744 | 2610 | Slave Sensor No. 50 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
786 | 9745 | 2611 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
787 | 9746 | 2612 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
788 | 9747 | 2613 |  | Reserved |  | 0
789 | 9748 | 2614 | Slave Sensor No. 50 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
790 | 9749 | 2615 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
791 | 9750 | 2616 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
792 | 9751 | 2617 |  | Reserved |  | 0
793 | 9752 | 2618 | Slave Sensor No. 50 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
794 | 9753 | 2619 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
795 | 9754 | 261A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
796 | 9755 | 261B |  | Reserved |  | 0
797 | 9756 | 261C | Slave Sensor No. 50 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
798 | 9757 | 261D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
799 | 9758 | 261E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
800 | 9759 | 261F |  | Reserved |  | 0
801 | 9760 | 2620 | Slave Sensor No. 51 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
802 | 9761 | 2621 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
803 | 9762 | 2622 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
804 | 9763 | 2623 |  | Reserved |  | 0
805 | 9764 | 2624 | Slave Sensor No. 51 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
806 | 9765 | 2625 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
807 | 9766 | 2626 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
808 | 9767 | 2627 |  | Reserved |  | 0
809 | 9768 | 2628 | Slave Sensor No. 51 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
810 | 9769 | 2629 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
811 | 9770 | 262A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
812 | 9771 | 262B |  | Reserved |  | 0
813 | 9772 | 262C | Slave Sensor No. 51 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
814 | 9773 | 262D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
815 | 9774 | 262E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
816 | 9775 | 262F |  | Reserved |  | 0
817 | 9776 | 2630 | Slave Sensor No. 52 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
818 | 9777 | 2631 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
819 | 9778 | 2632 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
820 | 9779 | 2633 |  | Reserved |  | 0
821 | 9780 | 2634 | Slave Sensor No. 52 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
822 | 9781 | 2635 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
823 | 9782 | 2636 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
824 | 9783 | 2637 |  | Reserved |  | 0
825 | 9784 | 2638 | Slave Sensor No. 52 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
826 | 9785 | 2639 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
827 | 9786 | 263A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
828 | 9787 | 263B |  | Reserved |  | 0
829 | 9788 | 263C | Slave Sensor No. 52 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
830 | 9789 | 263D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
831 | 9790 | 263E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
832 | 9791 | 263F |  | Reserved |  | 0
833 | 9792 | 2640 | Slave Sensor No. 53 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
834 | 9793 | 2641 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
835 | 9794 | 2642 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
836 | 9795 | 2643 |  | Reserved |  | 0
837 | 9796 | 2644 | Slave Sensor No. 53 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
838 | 9797 | 2645 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
839 | 9798 | 2646 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
840 | 9799 | 2647 |  | Reserved |  | 0
841 | 9800 | 2648 | Slave Sensor No. 53 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
842 | 9801 | 2649 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
843 | 9802 | 264A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
844 | 9803 | 264B |  | Reserved |  | 0
845 | 9804 | 264C | Slave Sensor No. 53 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
846 | 9805 | 264D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
847 | 9806 | 264E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
848 | 9807 | 264F |  | Reserved |  | 0
849 | 9808 | 2650 | Slave Sensor No. 54 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
850 | 9809 | 2651 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
851 | 9810 | 2652 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
852 | 9811 | 2653 |  | Reserved |  | 0
853 | 9812 | 2654 | Slave Sensor No. 54 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
854 | 9813 | 2655 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
855 | 9814 | 2656 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
856 | 9815 | 2657 |  | Reserved |  | 0
857 | 9816 | 2658 | Slave Sensor No. 54 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
858 | 9817 | 2659 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
859 | 9818 | 265A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
860 | 9819 | 265B |  | Reserved |  | 0
861 | 9820 | 265C | Slave Sensor No. 54 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
862 | 9821 | 265D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
863 | 9822 | 265E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
864 | 9823 | 265F |  | Reserved |  | 0
865 | 9824 | 2660 | Slave Sensor No. 55 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
866 | 9825 | 2661 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
867 | 9826 | 2662 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
868 | 9827 | 2663 |  | Reserved |  | 0
869 | 9828 | 2664 | Slave Sensor No. 55 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
870 | 9829 | 2665 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
871 | 9830 | 2666 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
872 | 9831 | 2667 |  | Reserved |  | 0
873 | 9832 | 2668 | Slave Sensor No. 55 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
874 | 9833 | 2669 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
875 | 9834 | 266A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
876 | 9835 | 266B |  | Reserved |  | 0
877 | 9836 | 266C | Slave Sensor No. 55 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
878 | 9837 | 266D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
879 | 9838 | 266E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
880 | 9839 | 266F |  | Reserved |  | 0
881 | 9840 | 2670 | Slave Sensor No. 56 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
882 | 9841 | 2671 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
883 | 9842 | 2672 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
884 | 9843 | 2673 |  | Reserved |  | 0
885 | 9844 | 2674 | Slave Sensor No. 56 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
886 | 9845 | 2675 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
887 | 9846 | 2676 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
888 | 9847 | 2677 |  | Reserved |  | 0
889 | 9848 | 2678 | Slave Sensor No. 56 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
890 | 9849 | 2679 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
891 | 9850 | 267A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
892 | 9851 | 267B |  | Reserved |  | 0
893 | 9852 | 267C | Slave Sensor No. 56 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
894 | 9853 | 267D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
895 | 9854 | 267E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
896 | 9855 | 267F |  | Reserved |  | 0
897 | 9856 | 2680 | Slave Sensor No. 57 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
898 | 9857 | 2681 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
899 | 9858 | 2682 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
900 | 9859 | 2683 |  | Reserved |  | 0
901 | 9860 | 2684 | Slave Sensor No. 57 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
902 | 9861 | 2685 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
903 | 9862 | 2686 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
904 | 9863 | 2687 |  | Reserved |  | 0
905 | 9864 | 2688 | Slave Sensor No. 57 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
906 | 9865 | 2689 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
907 | 9866 | 268A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
908 | 9867 | 268B |  | Reserved |  | 0
909 | 9868 | 268C | Slave Sensor No. 57 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
910 | 9869 | 268D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
911 | 9870 | 268E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
912 | 9871 | 268F |  | Reserved |  | 0
913 | 9872 | 2690 | Slave Sensor No. 58 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
914 | 9873 | 2691 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
915 | 9874 | 2692 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
916 | 9875 | 2693 |  | Reserved |  | 0
917 | 9876 | 2694 | Slave Sensor No. 58 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
918 | 9877 | 2695 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
919 | 9878 | 2696 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
920 | 9879 | 2697 |  | Reserved |  | 0
921 | 9880 | 2698 | Slave Sensor No. 58 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
922 | 9881 | 2699 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
923 | 9882 | 269A |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
924 | 9883 | 269B |  | Reserved |  | 0
925 | 9884 | 269C | Slave Sensor No. 58 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
926 | 9885 | 269D |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
927 | 9886 | 269E |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
928 | 9887 | 269F |  | Reserved |  | 0
929 | 9888 | 26A0 | Slave Sensor No. 59 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
930 | 9889 | 26A1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
931 | 9890 | 26A2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
932 | 9891 | 26A3 |  | Reserved |  | 0
933 | 9892 | 26A4 | Slave Sensor No. 59 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
934 | 9893 | 26A5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
935 | 9894 | 26A6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
936 | 9895 | 26A7 |  | Reserved |  | 0
937 | 9896 | 26A8 | Slave Sensor No. 59 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
938 | 9897 | 26A9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
939 | 9898 | 26AA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
940 | 9899 | 26AB |  | Reserved |  | 0
941 | 9900 | 26AC | Slave Sensor No. 59 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
942 | 9901 | 26AD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
943 | 9902 | 26AE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
944 | 9903 | 26AF |  | Reserved |  | 0
945 | 9904 | 26B0 | Slave Sensor No. 60 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
946 | 9905 | 26B1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
947 | 9906 | 26B2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
948 | 9907 | 26B3 |  | Reserved |  | 0
949 | 9908 | 26B4 | Slave Sensor No. 60 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
950 | 9909 | 26B5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
951 | 9910 | 26B6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
952 | 9911 | 26B7 |  | Reserved |  | 0
953 | 9912 | 26B8 | Slave Sensor No. 60 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
954 | 9913 | 26B9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
955 | 9914 | 26BA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
956 | 9915 | 26BB |  | Reserved |  | 0
957 | 9916 | 26BC | Slave Sensor No. 60 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
958 | 9917 | 26BD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
959 | 9918 | 26BE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
960 | 9919 | 26BF |  | Reserved |  | 0
961 | 9920 | 26C0 | Slave Sensor No. 61 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
962 | 9921 | 26C1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
963 | 9922 | 26C2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
964 | 9923 | 26C3 |  | Reserved |  | 0
965 | 9924 | 26C4 | Slave Sensor No. 61 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
966 | 9925 | 26C5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
967 | 9926 | 26C6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
968 | 9927 | 26C7 |  | Reserved |  | 0
969 | 9928 | 26C8 | Slave Sensor No. 61 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
970 | 9929 | 26C9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
971 | 9930 | 26CA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
972 | 9931 | 26CB |  | Reserved |  | 0
973 | 9932 | 26CC | Slave Sensor No. 61 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
974 | 9933 | 26CD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
975 | 9934 | 26CE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
976 | 9935 | 26CF |  | Reserved |  | 0
977 | 9936 | 26D0 | Slave Sensor No. 62 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
978 | 9937 | 26D1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
979 | 9938 | 26D2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
980 | 9939 | 26D3 |  | Reserved |  | 0
981 | 9940 | 26D4 | Slave Sensor No. 62 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
982 | 9941 | 26D5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
983 | 9942 | 26D6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
984 | 9943 | 26D7 |  | Reserved |  | 0
985 | 9944 | 26D8 | Slave Sensor No. 62 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
986 | 9945 | 26D9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
987 | 9946 | 26DA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
988 | 9947 | 26DB |  | Reserved |  | 0
989 | 9948 | 26DC | Slave Sensor No. 62 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
990 | 9949 | 26DD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
991 | 9950 | 26DE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
992 | 9951 | 26DF |  | Reserved |  | 0
993 | 9952 | 26E0 | Slave Sensor No. 63 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
994 | 9953 | 26E1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
995 | 9954 | 26E2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
996 | 9955 | 26E3 |  | Reserved |  | 0
997 | 9956 | 26E4 | Slave Sensor No. 63 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
998 | 9957 | 26E5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
999 | 9958 | 26E6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
1000 | 9959 | 26E7 |  | Reserved |  | 0
1001 | 9960 | 26E8 | Slave Sensor No. 63 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
1002 | 9961 | 26E9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
1003 | 9962 | 26EA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
1004 | 9963 | 26EB |  | Reserved |  | 0
1005 | 9964 | 26EC | Slave Sensor No. 63 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method： 0:Unable 1:> 2:<
1006 | 9965 | 26ED |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
1007 | 9966 | 26EE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
1008 | 9967 | 26EF |  | Reserved |  | 0
1009 | 9968 | 26F0 | Slave Sensor No. 64 higher limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
1010 | 9969 | 26F1 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
1011 | 9970 | 26F2 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
1012 | 9971 | 26F3 |  | Reserved |  | 0
1013 | 9972 | 26F4 | Slave Sensor No. 64 high limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
1014 | 9973 | 26F5 |  | Set current limited value | Unsigned 16 bit | 200 | 0-65535 | A/10 | *10
1015 | 9974 | 26F6 |  | Set temperature limited value | Unsigned 16 bit | 700 | 0-65535 | ℃/10 | *10
1016 | 9975 | 26F7 |  | Reserved |  | 0
1017 | 9976 | 26F8 | Slave Sensor No. 64 low limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
1018 | 9977 | 26F9 |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
1019 | 9978 | 26FA |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
1020 | 9979 | 26FB |  | Reserved |  | 0
1021 | 9980 | 26FC | Slave Sensor No. 64 lower limited value | Alarm No. + Comparison method | Unsigned 16 bit |  |  | —— | Comparison method：0:Unable 1:> 2:<
1022 | 9981 | 26FD |  | Set current limited value | Unsigned 16 bit | 0 | 0-65535 | A/10 | *10
1023 | 9982 | 26FE |  | Set temperature limited value | Unsigned 16 bit | 0 | 0-65535 | ℃/10 | *10
1024 | 9983 | 26FF |  | Reserved |  | 0

## 2XXX（Ethernet Parameter）
Ethernet Parameter(function code 03 read, 06/10 write)
No. | address Decimal | address Hexadecimal | Type | Name | Default | Range | Mark
1 | 10496 | 2900 | Network Parameter | IP addresss 0-1 | 0xC0A8 | 0～65535 | 192.168.0.200
2 | 10497 | 2901 |  | IP addresss 2-3 | 0x00C8 | 0～65535
3 | 10498 | 2902 |  | Subnet mask 0-1 | 0xFFFF | 0～65535 | 255.255.255.0
4 | 10499 | 2903 |  | Subnet mask 2-3 | 0xFF00 | 0～65535
5 | 10500 | 2904 |  | default gateway 0-1 | 0xC0A8 | 0～65535 | 192.168.0.254
6 | 10501 | 2905 |  | default gateway 2-3 | 0x00FE | 0～65535
7 | 10502 | 2906 |  | Client IP0-1 | 0x743E | 0～65535 | 116.62.67.131
8 | 10503 | 2907 |  | Client IP2-3 | 0x4383 | 0～65535
9 | 10504 | 2908 |  | Mode Selection | 0 | 0-1 | 0：SERVER 1:CLIENT
10 | 10505 | 2909 |  | Protocol | 0 | Not used yet
11 | 10506 | 290A |  | Client Port | 1883 | 0-65535 | 1883
12 | 10507 | 290B |  | DHCP | 0 | 0-1 | 0:close 1：open
13 | 10508 | 290C |  | linkdetInternel | 0 | Not used yet
14 | 10509 | 290D |  | reconnect time | 5 | 1-65535 | it won't work if 65535
15 | 10510 | 290E |  | push interval | 1 | 1-600 | second
16 | 10511 | 290F |  | Qos | 1 | 0-2
17 | 10512 | 2910 | password | the 1-2 number/letter of Domain Name | 0 | 0-127
18 | 10513 | 2911 |  | the 3-4 number/letter of Domain Name | 0 | 0-127
19 | 10514 | 2912 |  | the 5-6 number/letter of Domain Name | 0 | 0-127
20 | 10515 | 2913 |  | the 7-8 number/letter of Domain Name | 0 | 0-127
21 | 10516 | 2914 |  | the 9-10 number/letter of Domain Name | 0 | 0-127
22 | 10517 | 2915 |  | the 11-12 number/letter of Domain Name | 0 | 0-127
23 | 10518 | 2916 |  | the 13-14 number/letter of Domain Name | 0 | 0-127
24 | 10519 | 2917 |  | the 15-16 number/letter of Domain Name | 0 | 0-127
25 | 10520 | 2918 |  | the 17-18 number/letter of Domain Name | 0 | 0-127
26 | 10521 | 2919 |  | the 19-20 number/letter of Domain Name | 0 | 0-127
27 | 10522 | 291A |  | the 21-22 number/letter of Domain Name | 0 | 0-127
28 | 10523 | 291B |  | the 23-24 number/letter of Domain Name | 0 | 0-127
29 | 10524 | 291C |  | the 25-26 number/letter of Domain Name | 0 | 0-127
30 | 10525 | 291D |  | the 27-28 number/letter of Domain Name | 0 | 0-127
31 | 10526 | 291E |  | the 29-30 number/letter of Domain Name | 0 | 0-127
32 | 10527 | 291F |  | the 31-32 number/letter of Domain Name | 0 | 0-127
33 | 10528 | 2920 |  | the 33-34 number/letter of Domain Name | 0 | 0-127
34 | 10529 | 2921 |  | the 35-36 number/letter of Domain Name | 0 | 0-127
35 | 10530 | 2922 |  | the 37-38 number/letter of Domain Name | 0 | 0-127
36 | 10531 | 2923 |  | the 39-40 number/letter of Domain Name | 0 | 0-127
37 | 10532 | 2924 |  | the 41-42 number/letter of Domain Name | 0 | 0-127
38 | 10533 | 2925 |  | the 43-44 number/letter of Domain Name | 0 | 0-127
39 | 10534 | 2926 |  | the 45-46 number/letter of Domain Name | 0 | 0-127
40 | 10535 | 2927 |  | the 47-48 number/letter of Domain Name | 0 | 0-127
41 | 10536 | 2928 |  | the 49-50 number/letter of Domain Name | 0 | 0-127
42 | 10537 | 2929 |  | the 51-52 number/letter of Domain Name | 0 | 0-127
43 | 10538 | 292A |  | the 53-54 number/letter of Domain Name | 0 | 0-127
44 | 10539 | 292B |  | the 55-56 number/letter of Domain Name | 0 | 0-127
45 | 10540 | 292C |  | the 57-58 number/letter of Domain Name | 0 | 0-127
46 | 10541 | 292D |  | the 59-60 number/letter of Domain Name | 0 | 0-127
47 | 10542 | 292E |  | the 61-62 number/letter of Domain Name | 0 | 0-127
48 | 10543 | 292F |  | the 63-64 number/letter of Domain Name | 0 | 0-127
49 | 10544 | 2930 | User name | the 1-2 number/letter of Domain Name |  | 0-127
50 | 10545 | 2931 |  | the 3-4 number/letter of Domain Name |  | 0-127
51 | 10546 | 2932 |  | the 5-6 number/letter of Domain Name |  | 0-127
52 | 10547 | 2933 |  | the 7-8 number/letter of Domain Name |  | 0-127
53 | 10548 | 2934 |  | the 9-10 number/letter of Domain Name |  | 0-127
54 | 10549 | 2935 |  | the 11-12 number/letter of Domain Name |  | 0-127
55 | 10550 | 2936 |  | the 13-14 number/letter of Domain Name |  | 0-127
56 | 10551 | 2937 |  | the 15-16 number/letter of Domain Name |  | 0-127
57 | 10552 | 2938 |  | the 17-18 number/letter of Domain Name |  | 0-127
58 | 10553 | 2939 |  | the 19-20 number/letter of Domain Name |  | 0-127
59 | 10554 | 293A |  | the 21-22 number/letter of Domain Name |  | 0-127
60 | 10555 | 293B |  | the 23-24 number/letter of Domain Name |  | 0-127
61 | 10556 | 293C |  | the 25-26 number/letter of Domain Name |  | 0-127
62 | 10557 | 293D |  | the 27-28 number/letter of Domain Name |  | 0-127
63 | 10558 | 293E |  | the 29-30 number/letter of Domain Name |  | 0-127
64 | 10559 | 293F |  | the 31-32 number/letter of Domain Name |  | 0-127
65 | 10560 | 2940 |  | the 33-34 number/letter of Domain Name |  | 0-127
66 | 10561 | 2941 |  | the 35-36 number/letter of Domain Name |  | 0-127
67 | 10562 | 2942 |  | the 37-38 number/letter of Domain Name |  | 0-127
68 | 10563 | 2943 |  | the 39-40 number/letter of Domain Name |  | 0-127
69 | 10564 | 2944 |  | the 41-42 number/letter of Domain Name |  | 0-127
70 | 10565 | 2945 |  | the 43-44 number/letter of Domain Name | 0 | 0-127
71 | 10566 | 2946 |  | the 45-46 number/letter of Domain Name | 0 | 0-127
72 | 10567 | 2947 |  | the 47-48 number/letter of Domain Name | 0 | 0-127
73 | 10568 | 2948 |  | the 49-50 number/letter of Domain Name | 0 | 0-127
74 | 10569 | 2949 |  | the 51-52 number/letter of Domain Name | 0 | 0-127
75 | 10570 | 294A |  | the 53-54 number/letter of Domain Name | 0 | 0-127
76 | 10571 | 294B |  | the 55-56 number/letter of Domain Name | 0 | 0-127
77 | 10572 | 294C |  | the 57-58 number/letter of Domain Name | 0 | 0-127
78 | 10573 | 294D |  | the 59-60 number/letter of Domain Name | 0 | 0-127
79 | 10574 | 294E |  | the 61-62 number/letter of Domain Name | 0 | 0-127
80 | 10575 | 294F |  | the 63-64 number/letter of Domain Name | 0 | 0-127
81 | 10576 | 2950 | ClientID | the 1-2 number/letter of Domain Name | 0 | 0-127
82 | 10577 | 2951 |  | the 3-4 number/letter of Domain Name | 0 | 0-127
83 | 10578 | 2952 |  | the 5-6 number/letter of Domain Name | 0 | 0-127
84 | 10579 | 2953 |  | the 7-8 number/letter of Domain Name | 0 | 0-127
85 | 10580 | 2954 |  | the 9-10 number/letter of Domain Name | 0 | 0-127
86 | 10581 | 2955 |  | the 11-12 number/letter of Domain Name | 0 | 0-127
87 | 10582 | 2956 |  | the 13-14 number/letter of Domain Name | 0 | 0-127
88 | 10583 | 2957 |  | the 15-16 number/letter of Domain Name | 0 | 0-127
89 | 10584 | 2958 |  | the 17-18 number/letter of Domain Name | 0 | 0-127
90 | 10585 | 2959 |  | the 19-20 number/letter of Domain Name | 0 | 0-127
91 | 10586 | 295A |  | the 21-22 number/letter of Domain Name | 0 | 0-127
92 | 10587 | 295B |  | the 23-24 number/letter of Domain Name | 0 | 0-127
93 | 10588 | 295C |  | the 25-26 number/letter of Domain Name | 0 | 0-127
94 | 10589 | 295D |  | the 27-28 number/letter of Domain Name | 0 | 0-127
95 | 10590 | 295E |  | the 29-30 number/letter of Domain Name | 0 | 0-127
96 | 10591 | 295F |  | the 31-32 number/letter of Domain Name | 0 | 0-127
97 | 10592 | 2960 |  | the 33-34 number/letter of Domain Name | 0 | 0-127
98 | 10593 | 2961 |  | the 35-36 number/letter of Domain Name | 0 | 0-127
99 | 10594 | 2962 |  | the 37-38 number/letter of Domain Name | 0 | 0-127
100 | 10595 | 2963 |  | the 39-40 number/letter of Domain Name | 0 | 0-127
101 | 10596 | 2964 |  | the 41-42 number/letter of Domain Name | 0 | 0-127
102 | 10597 | 2965 |  | the 43-44 number/letter of Domain Name | 0 | 0-127
103 | 10598 | 2966 |  | the 45-46 number/letter of Domain Name | 0 | 0-127
104 | 10599 | 2967 |  | the 47-48 number/letter of Domain Name | 0 | 0-127
105 | 10600 | 2968 |  | the 49-50 number/letter of Domain Name | 0 | 0-127
106 | 10601 | 2969 |  | the 51-52 number/letter of Domain Name | 0 | 0-127
107 | 10602 | 296A |  | the 53-54 number/letter of Domain Name | 0 | 0-127
108 | 10603 | 296B |  | the 55-56 number/letter of Domain Name | 0 | 0-127
109 | 10604 | 296C |  | the 57-58 number/letter of Domain Name | 0 | 0-127
110 | 10605 | 296D |  | the 59-60 number/letter of Domain Name | 0 | 0-127
111 | 10606 | 296E |  | the 61-62 number/letter of Domain Name | 0 | 0-127
112 | 10607 | 296F |  | the 63-64 number/letter of Domain Name | 0 | 0-127

## 2XXX（Shielding Parameter）
Shielding Parameter(function code 03 read,06/10write)
No. | address Decimal | address Hexadecimal | Name | Default | Range | Mark
1 | 10752 | 2A00 | Slave Sensor 1 | 0x24 | 0-65535 | Meaning：0：close shielding 1：open shielding the shielding flag from low bit to high bit: bit 0 open/close alarm bit 1 offline fault bit 2 current over-limit alarm bit 3 temperature over-limit alarm bit 4 Trend change alarm bit 5 current trend change(alarm+real) bit 6 temperature trend change(alarm+real)
2 | 10753 | 2A01 | Slave Sensor 2 | 0x24 | 0-65535
3 | 10754 | 2A02 | Slave Sensor 3 | 0x24 | 0-65535
4 | 10755 | 2A03 | Slave Sensor 4 | 0x24 | 0-65535
5 | 10756 | 2A04 | Slave Sensor 5 | 0x24 | 0-65535
6 | 10757 | 2A05 | Slave Sensor 6 | 0x24 | 0-65535
7 | 10758 | 2A06 | Slave Sensor 7 | 0x24 | 0-65535
8 | 10759 | 2A07 | Slave Sensor 8 | 0x24 | 0-65535
9 | 10760 | 2A08 | Slave Sensor 9 | 0x24 | 0-65535
10 | 10761 | 2A09 | Slave Sensor 10 | 0x24 | 0-65535
11 | 10762 | 2A0A | Slave Sensor 11 | 0x24 | 0-65535
12 | 10763 | 2A0B | Slave Sensor 12 | 0x24 | 0-65535
13 | 10764 | 2A0C | Slave Sensor 13 | 0x24 | 0-65535
14 | 10765 | 2A0D | Slave Sensor 14 | 0x24 | 0-65535
15 | 10766 | 2A0E | Slave Sensor 15 | 0x24 | 0-65535
16 | 10767 | 2A0F | Slave Sensor 16 | 0x24 | 0-65535
17 | 10768 | 2A10 | Slave Sensor 17 | 0x24 | 0-65535
18 | 10769 | 2A11 | Slave Sensor 18 | 0x24 | 0-65535
19 | 10770 | 2A12 | Slave Sensor 19 | 0x24 | 0-65535
20 | 10771 | 2A13 | Slave Sensor 20 | 0x24 | 0-65535
21 | 10772 | 2A14 | Slave Sensor 21 | 0x24 | 0-65535
22 | 10773 | 2A15 | Slave Sensor 22 | 0x24 | 0-65535
23 | 10774 | 2A16 | Slave Sensor 23 | 0x24 | 0-65535
24 | 10775 | 2A17 | Slave Sensor 24 | 0x24 | 0-65535
25 | 10776 | 2A18 | Slave Sensor 25 | 0x24 | 0-65535
26 | 10777 | 2A19 | Slave Sensor 26 | 0x24 | 0-65535
27 | 10778 | 2A1A | Slave Sensor 27 | 0x24 | 0-65535
28 | 10779 | 2A1B | Slave Sensor 28 | 0x24 | 0-65535
29 | 10780 | 2A1C | Slave Sensor 29 | 0x24 | 0-65535
30 | 10781 | 2A1D | Slave Sensor 30 | 0x24 | 0-65535
31 | 10782 | 2A1E | Slave Sensor 31 | 0x24 | 0-65535
32 | 10783 | 2A1F | Slave Sensor 32 | 0x24 | 0-65535
33 | 10784 | 2A20 | Slave Sensor 33 | 0x24 | 0-65535
34 | 10785 | 2A21 | Slave Sensor 34 | 0x24 | 0-65535
35 | 10786 | 2A22 | Slave Sensor 35 | 0x24 | 0-65535
36 | 10787 | 2A23 | Slave Sensor 36 | 0x24 | 0-65535
37 | 10788 | 2A24 | Slave Sensor 37 | 0x24 | 0-65535
38 | 10789 | 2A25 | Slave Sensor 38 | 0x24 | 0-65535
39 | 10790 | 2A26 | Slave Sensor 39 | 0x24 | 0-65535
40 | 10791 | 2A27 | Slave Sensor 40 | 0x24 | 0-65535
41 | 10792 | 2A28 | Slave Sensor 41 | 0x24 | 0-65535
42 | 10793 | 2A29 | Slave Sensor 42 | 0x24 | 0-65535
43 | 10794 | 2A2A | Slave Sensor 43 | 0x24 | 0-65535
44 | 10795 | 2A2B | Slave Sensor 44 | 0x24 | 0-65535
45 | 10796 | 2A2C | Slave Sensor 45 | 0x24 | 0-65535
46 | 10797 | 2A2D | Slave Sensor 46 | 0x24 | 0-65535
47 | 10798 | 2A2E | Slave Sensor 47 | 0x24 | 0-65535
48 | 10799 | 2A2F | Slave Sensor 48 | 0x24 | 0-65535
49 | 10800 | 2A30 | Slave Sensor 49 | 0x24 | 0-65535
50 | 10801 | 2A31 | Slave Sensor 50 | 0x24 | 0-65535
51 | 10802 | 2A32 | Slave Sensor 51 | 0x24 | 0-65535
52 | 10803 | 2A33 | Slave Sensor 52 | 0x24 | 0-65535
53 | 10804 | 2A34 | Slave Sensor 53 | 0x24 | 0-65535
54 | 10805 | 2A35 | Slave Sensor 54 | 0x24 | 0-65535
55 | 10806 | 2A36 | Slave Sensor 55 | 0x24 | 0-65535
56 | 10807 | 2A37 | Slave Sensor 56 | 0x24 | 0-65535
57 | 10808 | 2A38 | Slave Sensor 57 | 0x24 | 0-65535
58 | 10809 | 2A39 | Slave Sensor 58 | 0x24 | 0-65535
59 | 10810 | 2A3A | Slave Sensor 59 | 0x24 | 0-65535
60 | 10811 | 2A3B | Slave Sensor 60 | 0x24 | 0-65535
61 | 10812 | 2A3C | Slave Sensor 61 | 0x24 | 0-65535
62 | 10813 | 2A3D | Slave Sensor 62 | 0x24 | 0-65535
63 | 10814 | 2A3E | Slave Sensor 63 | 0x24 | 0-65535
64 | 10815 | 2A3F | Slave Sensor 64 | 0x24 | 0-65535

## 3XXX（real-time clock）
Real Time Clock( (function code 03/06/10 read/write)
No. | address Decimal | address Hexadecimal | Name | Data Type | Default | Range | uint | Mark
1 | 12800 | 3200 | Year | Unsigned 16 bit | 2019 | 2019～2100 | Year
2 | 12801 | 3201 | Date/Month | Unsigned 16 bit | 0x0701 | 0x0101～0x1F0C | Date/Month | high bit: date low bit: month
3 | 12802 | 3202 | Minite/Hour | Unsigned 16 bit | 0x1C09 | 0x0000～0x3B17 | Minite/Hour | high bit: minute low bit: hour
4 | 12803 | 3203 | Second | Unsigned 16 bit | 10 | 0～59 | Second

## 8XXX SOE
SOE event record (function code 03 read)
No. | address Decimal | address Hexadecimal |  | Name | Data Type | Default | Value Range | Mark
1 | 32768 | 8000 | the 1st record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-99 | Group：0 Member： 0：no SOE 1：Slave Sensor open 2：Slave Sensor close 3：Slave Sensor low battery 4：Slave Sensor off line 5：Slave Sensor on line
2 | 32769 | 8001 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-12
3 | 32770 | 8002 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-23
4 | 32771 | 8003 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-59
5 | 32772 | 8004 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1000
6 | 32773 | 8005 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
7 | 32774 | 8006
8 | 32775 | 8007 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
9 | 32776 | 8008 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
10 | 32777 | 8009 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
11 | 32778 | 800A
12 | 32779 | 800B | the 2nd record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-99
13 | 32780 | 800C |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-12
14 | 32781 | 800D |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-23
15 | 32782 | 800E |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-59
16 | 32783 | 800F |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1000
17 | 32784 | 8010 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
18 | 32785 | 8011
19 | 32786 | 8012 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
20 | 32787 | 8013 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
21 | 32788 | 8014 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
22 | 32789 | 8015
23 | 32790 | 8016 | the 3rd record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-100
24 | 32791 | 8017 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-13
25 | 32792 | 8018 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-24
26 | 32793 | 8019 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-60
27 | 32794 | 801A |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1001
28 | 32795 | 801B |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
29 | 32796 | 801C
30 | 32797 | 801D |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
31 | 32798 | 801E |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
32 | 32799 | 801F |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
33 | 32800 | 8020
34 | 32801 | 8021 | the 4th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-100
35 | 32802 | 8022 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-13
36 | 32803 | 8023 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-24
37 | 32804 | 8024 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-60
38 | 32805 | 8025 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1001
39 | 32806 | 8026 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
40 | 32807 | 8027
41 | 32808 | 8028 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
42 | 32809 | 8029 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
43 | 32810 | 802A |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
44 | 32811 | 802B
45 | 32812 | 802C | the 5th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-100
46 | 32813 | 802D |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-13
47 | 32814 | 802E |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-24
48 | 32815 | 802F |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-60
49 | 32816 | 8030 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1001
50 | 32817 | 8031 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
51 | 32818 | 8032
52 | 32819 | 8033 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
53 | 32820 | 8034 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
54 | 32821 | 8035 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
55 | 32822 | 8036
56 | 32823 | 8037 | the 6th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-100
57 | 32824 | 8038 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-13
58 | 32825 | 8039 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-24
59 | 32826 | 803A |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-60
60 | 32827 | 803B |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1001
61 | 32828 | 803C |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
62 | 32829 | 803D
63 | 32830 | 803E |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
64 | 32831 | 803F |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
65 | 32832 | 8040 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
66 | 32833 | 8041
67 | 32834 | 8042 | the 7th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-101
68 | 32835 | 8043 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-14
69 | 32836 | 8044 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-25
70 | 32837 | 8045 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-61
71 | 32838 | 8046 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1002
72 | 32839 | 8047 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
73 | 32840 | 8048
74 | 32841 | 8049 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
75 | 32842 | 804A |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
76 | 32843 | 804B |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
77 | 32844 | 804C
78 | 32845 | 804D | the 8th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-101
79 | 32846 | 804E |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-14
80 | 32847 | 804F |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-25
81 | 32848 | 8050 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-61
82 | 32849 | 8051 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1002
83 | 32850 | 8052 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
84 | 32851 | 8053
85 | 32852 | 8054 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
86 | 32853 | 8055 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
87 | 32854 | 8056 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
88 | 32855 | 8057
89 | 32856 | 8058 | the 9th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-101
90 | 32857 | 8059 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-14
91 | 32858 | 805A |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-25
92 | 32859 | 805B |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-61
93 | 32860 | 805C |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1002
94 | 32861 | 805D |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
95 | 32862 | 805E
96 | 32863 | 805F |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
97 | 32864 | 8060 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
98 | 32865 | 8061 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
99 | 32866 | 8062
100 | 32867 | 8063 | the 10th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-101
101 | 32868 | 8064 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-14
102 | 32869 | 8065 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-25
103 | 32870 | 8066 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-61
104 | 32871 | 8067 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1002
105 | 32872 | 8068 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
106 | 32873 | 8069
107 | 32874 | 806A |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
108 | 32875 | 806B |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
109 | 32876 | 806C |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
110 | 32877 | 806D
111 | 32878 | 806E | the 11th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-102
112 | 32879 | 806F |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-15
113 | 32880 | 8070 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-26
114 | 32881 | 8071 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-62
115 | 32882 | 8072 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1003
116 | 32883 | 8073 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
117 | 32884 | 8074
118 | 32885 | 8075 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
119 | 32886 | 8076 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
120 | 32887 | 8077 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
121 | 32888 | 8078
122 | 32889 | 8079 | the 12th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-102
123 | 32890 | 807A |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-15
124 | 32891 | 807B |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-26
125 | 32892 | 807C |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-62
126 | 32893 | 807D |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1003
127 | 32894 | 807E |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
128 | 32895 | 807F
129 | 32896 | 8080 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
130 | 32897 | 8081 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
131 | 32898 | 8082 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
132 | 32899 | 8083
133 | 32900 | 8084 | the 13th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-102
134 | 32901 | 8085 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-15
135 | 32902 | 8086 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-26
136 | 32903 | 8087 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-62
137 | 32904 | 8088 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1003
138 | 32905 | 8089 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
139 | 32906 | 808A
140 | 32907 | 808B |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
141 | 32908 | 808C |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
142 | 32909 | 808D |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
143 | 32910 | 808E
144 | 32911 | 808F | the 14th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-102
145 | 32912 | 8090 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-15
146 | 32913 | 8091 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-26
147 | 32914 | 8092 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-62
148 | 32915 | 8093 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1003
149 | 32916 | 8094 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
150 | 32917 | 8095
151 | 32918 | 8096 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
152 | 32919 | 8097 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
153 | 32920 | 8098 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
154 | 32921 | 8099
155 | 32922 | 809A | the 15th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-103
156 | 32923 | 809B |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-16
157 | 32924 | 809C |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-27
158 | 32925 | 809D |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-63
159 | 32926 | 809E |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1004
160 | 32927 | 809F |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
161 | 32928 | 80A0
162 | 32929 | 80A1 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
163 | 32930 | 80A2 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
164 | 32931 | 80A3 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
165 | 32932 | 80A4
166 | 32933 | 80A5 | the 16th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-103
167 | 32934 | 80A6 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-16
168 | 32935 | 80A7 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-27
169 | 32936 | 80A8 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-63
170 | 32937 | 80A9 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1004
171 | 32938 | 80AA |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
172 | 32939 | 80AB
173 | 32940 | 80AC |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
174 | 32941 | 80AD |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
175 | 32942 | 80AE |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
176 | 32943 | 80AF
177 | 32944 | 80B0 | the 17th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-103
178 | 32945 | 80B1 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-16
179 | 32946 | 80B2 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-27
180 | 32947 | 80B3 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-63
181 | 32948 | 80B4 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1004
182 | 32949 | 80B5 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
183 | 32950 | 80B6
184 | 32951 | 80B7 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
185 | 32952 | 80B8 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
186 | 32953 | 80B9 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
187 | 32954 | 80BA
188 | 32955 | 80BB | the 18th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-103
189 | 32956 | 80BC |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-16
190 | 32957 | 80BD |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-27
191 | 32958 | 80BE |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-63
192 | 32959 | 80BF |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1004
193 | 32960 | 80C0 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
194 | 32961 | 80C1
195 | 32962 | 80C2 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
196 | 32963 | 80C3 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
197 | 32964 | 80C4 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
198 | 32965 | 80C5
199 | 32966 | 80C6 | the 19th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-104
200 | 32967 | 80C7 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-17
201 | 32968 | 80C8 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-28
202 | 32969 | 80C9 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-64
203 | 32970 | 80CA |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1005
204 | 32971 | 80CB |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
205 | 32972 | 80CC
206 | 32973 | 80CD |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
207 | 32974 | 80CE |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
208 | 32975 | 80CF |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
209 | 32976 | 80D0
210 | 32977 | 80D1 | the 20th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-104
211 | 32978 | 80D2 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-17
212 | 32979 | 80D3 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-28
213 | 32980 | 80D4 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-64
214 | 32981 | 80D5 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1005
215 | 32982 | 80D6 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
216 | 32983 | 80D7
217 | 32984 | 80D8 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
218 | 32985 | 80D9 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
219 | 32986 | 80DA |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
220 | 32987 | 80DB
221 | 32988 | 80DC | the 21th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-104
222 | 32989 | 80DD |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-17
223 | 32990 | 80DE |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-28
224 | 32991 | 80DF |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-64
225 | 32992 | 80E0 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1005
226 | 32993 | 80E1 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
227 | 32994 | 80E2
228 | 32995 | 80E3 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
229 | 32996 | 80E4 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
230 | 32997 | 80E5 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
231 | 32998 | 80E6
232 | 32999 | 80E7 | the 22th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-104
233 | 33000 | 80E8 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-17
234 | 33001 | 80E9 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-28
235 | 33002 | 80EA |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-64
236 | 33003 | 80EB |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1005
237 | 33004 | 80EC |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
238 | 33005 | 80ED
239 | 33006 | 80EE |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
240 | 33007 | 80EF |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
241 | 33008 | 80F0 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
242 | 33009 | 80F1
243 | 33010 | 80F2 | the 23th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-105
244 | 33011 | 80F3 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-18
245 | 33012 | 80F4 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-29
246 | 33013 | 80F5 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-65
247 | 33014 | 80F6 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1006
248 | 33015 | 80F7 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
249 | 33016 | 80F8
250 | 33017 | 80F9 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
251 | 33018 | 80FA |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
252 | 33019 | 80FB |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
253 | 33020 | 80FC
254 | 33021 | 80FD | the 24th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-105
255 | 33022 | 80FE |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-18
256 | 33023 | 80FF |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-29
257 | 33024 | 8100 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-65
258 | 33025 | 8101 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1006
259 | 33026 | 8102 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
260 | 33027 | 8103
261 | 33028 | 8104 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
262 | 33029 | 8105 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
263 | 33030 | 8106 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
264 | 33031 | 8107
265 | 33032 | 8108 | the 25th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-105
266 | 33033 | 8109 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-18
267 | 33034 | 810A |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-29
268 | 33035 | 810B |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-65
269 | 33036 | 810C |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1006
270 | 33037 | 810D |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
271 | 33038 | 810E
272 | 33039 | 810F |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
273 | 33040 | 8110 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
274 | 33041 | 8111 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
275 | 33042 | 8112
276 | 33043 | 8113 | the 26th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-105
277 | 33044 | 8114 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-18
278 | 33045 | 8115 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-29
279 | 33046 | 8116 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-65
280 | 33047 | 8117 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1006
281 | 33048 | 8118 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
282 | 33049 | 8119
283 | 33050 | 811A |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
284 | 33051 | 811B |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
285 | 33052 | 811C |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
286 | 33053 | 811D
287 | 33054 | 811E | the 27th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-106
288 | 33055 | 811F |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-19
289 | 33056 | 8120 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-30
290 | 33057 | 8121 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-66
291 | 33058 | 8122 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1007
292 | 33059 | 8123 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
293 | 33060 | 8124
294 | 33061 | 8125 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
295 | 33062 | 8126 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
296 | 33063 | 8127 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
297 | 33064 | 8128
298 | 33065 | 8129 | the 28th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-106
299 | 33066 | 812A |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-19
300 | 33067 | 812B |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-30
301 | 33068 | 812C |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-66
302 | 33069 | 812D |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1007
303 | 33070 | 812E |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
304 | 33071 | 812F
305 | 33072 | 8130 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
306 | 33073 | 8131 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
307 | 33074 | 8132 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
308 | 33075 | 8133
309 | 33076 | 8134 | the 29th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-106
310 | 33077 | 8135 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-19
311 | 33078 | 8136 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-30
312 | 33079 | 8137 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-66
313 | 33080 | 8138 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1007
314 | 33081 | 8139 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
315 | 33082 | 813A
316 | 33083 | 813B |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
317 | 33084 | 813C |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
318 | 33085 | 813D |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
319 | 33086 | 813E
320 | 33087 | 813F | the 30th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-106
321 | 33088 | 8140 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-19
322 | 33089 | 8141 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-30
323 | 33090 | 8142 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-66
324 | 33091 | 8143 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1007
325 | 33092 | 8144 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
326 | 33093 | 8145
327 | 33094 | 8146 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
328 | 33095 | 8147 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
329 | 33096 | 8148 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
330 | 33097 | 8149
331 | 33098 | 814A | the 31th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-107
332 | 33099 | 814B |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-20
333 | 33100 | 814C |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-31
334 | 33101 | 814D |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-67
335 | 33102 | 814E |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1008
336 | 33103 | 814F |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
337 | 33104 | 8150
338 | 33105 | 8151 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
339 | 33106 | 8152 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
340 | 33107 | 8153 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
341 | 33108 | 8154
342 | 33109 | 8155 | the 32th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-107
343 | 33110 | 8156 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-20
344 | 33111 | 8157 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-31
345 | 33112 | 8158 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-67
346 | 33113 | 8159 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1008
347 | 33114 | 815A |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
348 | 33115 | 815B
349 | 33116 | 815C |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
350 | 33117 | 815D |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
351 | 33118 | 815E |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
352 | 33119 | 815F
353 | 33120 | 8160 | the 33th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-107
354 | 33121 | 8161 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-20
355 | 33122 | 8162 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-31
356 | 33123 | 8163 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-67
357 | 33124 | 8164 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1008
358 | 33125 | 8165 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
359 | 33126 | 8166
360 | 33127 | 8167 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
361 | 33128 | 8168 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
362 | 33129 | 8169 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
363 | 33130 | 816A
364 | 33131 | 816B | the 34th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-107
365 | 33132 | 816C |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-20
366 | 33133 | 816D |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-31
367 | 33134 | 816E |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-67
368 | 33135 | 816F |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1008
369 | 33136 | 8170 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
370 | 33137 | 8171
371 | 33138 | 8172 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
372 | 33139 | 8173 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
373 | 33140 | 8174 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
374 | 33141 | 8175
375 | 33142 | 8176 | the 35th record | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-108
376 | 33143 | 8177 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-21
377 | 33144 | 8178 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-32
378 | 33145 | 8179 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-68
379 | 33146 | 817A |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1009
380 | 33147 | 817B |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
381 | 33148 | 817C
382 | 33149 | 817D |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
383 | 33150 | 817E |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
384 | 33151 | 817F |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
385 | 33152 | 8180
386 | 33153 | 8181 | 第36条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-108
387 | 33154 | 8182 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-21
388 | 33155 | 8183 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-32
389 | 33156 | 8184 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-68
390 | 33157 | 8185 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1009
391 | 33158 | 8186 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
392 | 33159 | 8187
393 | 33160 | 8188 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
394 | 33161 | 8189 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
395 | 33162 | 818A |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
396 | 33163 | 818B
397 | 33164 | 818C | 第37条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-108
398 | 33165 | 818D |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-21
399 | 33166 | 818E |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-32
400 | 33167 | 818F |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-68
401 | 33168 | 8190 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1009
402 | 33169 | 8191 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
403 | 33170 | 8192
404 | 33171 | 8193 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
405 | 33172 | 8194 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
406 | 33173 | 8195 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
407 | 33174 | 8196
408 | 33175 | 8197 | 第38条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-108
409 | 33176 | 8198 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-21
410 | 33177 | 8199 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-32
411 | 33178 | 819A |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-68
412 | 33179 | 819B |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1009
413 | 33180 | 819C |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
414 | 33181 | 819D
415 | 33182 | 819E |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
416 | 33183 | 819F |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
417 | 33184 | 81A0 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
418 | 33185 | 81A1
419 | 33186 | 81A2 | 第39条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-109
420 | 33187 | 81A3 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-22
421 | 33188 | 81A4 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-33
422 | 33189 | 81A5 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-69
423 | 33190 | 81A6 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1010
424 | 33191 | 81A7 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
425 | 33192 | 81A8
426 | 33193 | 81A9 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
427 | 33194 | 81AA |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
428 | 33195 | 81AB |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
429 | 33196 | 81AC
430 | 33197 | 81AD | 第40条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-109
431 | 33198 | 81AE |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-22
432 | 33199 | 81AF |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-33
433 | 33200 | 81B0 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-69
434 | 33201 | 81B1 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1010
435 | 33202 | 81B2 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
436 | 33203 | 81B3
437 | 33204 | 81B4 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
438 | 33205 | 81B5 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
439 | 33206 | 81B6 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
440 | 33207 | 81B7
441 | 33208 | 81B8 | 第41条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-109
442 | 33209 | 81B9 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-22
443 | 33210 | 81BA |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-33
444 | 33211 | 81BB |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-69
445 | 33212 | 81BC |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1010
446 | 33213 | 81BD |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
447 | 33214 | 81BE
448 | 33215 | 81BF |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
449 | 33216 | 81C0 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
450 | 33217 | 81C1 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
451 | 33218 | 81C2
452 | 33219 | 81C3 | 第42条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-109
453 | 33220 | 81C4 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-22
454 | 33221 | 81C5 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-33
455 | 33222 | 81C6 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-69
456 | 33223 | 81C7 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1010
457 | 33224 | 81C8 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
458 | 33225 | 81C9
459 | 33226 | 81CA |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
460 | 33227 | 81CB |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
461 | 33228 | 81CC |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
462 | 33229 | 81CD
463 | 33230 | 81CE | 第43条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-110
464 | 33231 | 81CF |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-23
465 | 33232 | 81D0 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-34
466 | 33233 | 81D1 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-70
467 | 33234 | 81D2 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1011
468 | 33235 | 81D3 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
469 | 33236 | 81D4
470 | 33237 | 81D5 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
471 | 33238 | 81D6 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
472 | 33239 | 81D7 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
473 | 33240 | 81D8
474 | 33241 | 81D9 | 第44条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-110
475 | 33242 | 81DA |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-23
476 | 33243 | 81DB |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-34
477 | 33244 | 81DC |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-70
478 | 33245 | 81DD |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1011
479 | 33246 | 81DE |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
480 | 33247 | 81DF
481 | 33248 | 81E0 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
482 | 33249 | 81E1 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
483 | 33250 | 81E2 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
484 | 33251 | 81E3
485 | 33252 | 81E4 | 第45条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-110
486 | 33253 | 81E5 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-23
487 | 33254 | 81E6 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-34
488 | 33255 | 81E7 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-70
489 | 33256 | 81E8 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1011
490 | 33257 | 81E9 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
491 | 33258 | 81EA
492 | 33259 | 81EB |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
493 | 33260 | 81EC |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
494 | 33261 | 81ED |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
495 | 33262 | 81EE
496 | 33263 | 81EF | 第46条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-110
497 | 33264 | 81F0 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-23
498 | 33265 | 81F1 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-34
499 | 33266 | 81F2 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-70
500 | 33267 | 81F3 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1011
501 | 33268 | 81F4 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
502 | 33269 | 81F5
503 | 33270 | 81F6 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
504 | 33271 | 81F7 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
505 | 33272 | 81F8 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
506 | 33273 | 81F9
507 | 33274 | 81FA | 第47条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-111
508 | 33275 | 81FB |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-24
509 | 33276 | 81FC |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-35
510 | 33277 | 81FD |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-71
511 | 33278 | 81FE |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1012
512 | 33279 | 81FF |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
513 | 33280 | 8200
514 | 33281 | 8201 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
515 | 33282 | 8202 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
516 | 33283 | 8203 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
517 | 33284 | 8204
518 | 33285 | 8205 | 第48条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-111
519 | 33286 | 8206 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-24
520 | 33287 | 8207 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-35
521 | 33288 | 8208 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-71
522 | 33289 | 8209 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1012
523 | 33290 | 820A |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
524 | 33291 | 820B
525 | 33292 | 820C |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
526 | 33293 | 820D |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
527 | 33294 | 820E |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
528 | 33295 | 820F
529 | 33296 | 8210 | 第49条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-111
530 | 33297 | 8211 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-24
531 | 33298 | 8212 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-35
532 | 33299 | 8213 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-71
533 | 33300 | 8214 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1012
534 | 33301 | 8215 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
535 | 33302 | 8216
536 | 33303 | 8217 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
537 | 33304 | 8218 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
538 | 33305 | 8219 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
539 | 33306 | 821A
540 | 33307 | 821B | 第50条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-111
541 | 33308 | 821C |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-24
542 | 33309 | 821D |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-35
543 | 33310 | 821E |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-71
544 | 33311 | 821F |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1012
545 | 33312 | 8220 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
546 | 33313 | 8221
547 | 33314 | 8222 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
548 | 33315 | 8223 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
549 | 33316 | 8224 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
550 | 33317 | 8225
551 | 33318 | 8226 | 第51条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-112
552 | 33319 | 8227 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-25
553 | 33320 | 8228 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-36
554 | 33321 | 8229 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-72
555 | 33322 | 822A |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1013
556 | 33323 | 822B |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
557 | 33324 | 822C
558 | 33325 | 822D |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
559 | 33326 | 822E |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
560 | 33327 | 822F |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
561 | 33328 | 8230
562 | 33329 | 8231 | 第52条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-112
563 | 33330 | 8232 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-25
564 | 33331 | 8233 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-36
565 | 33332 | 8234 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-72
566 | 33333 | 8235 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1013
567 | 33334 | 8236 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
568 | 33335 | 8237
569 | 33336 | 8238 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
570 | 33337 | 8239 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
571 | 33338 | 823A |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
572 | 33339 | 823B
573 | 33340 | 823C | 第53条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-112
574 | 33341 | 823D |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-25
575 | 33342 | 823E |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-36
576 | 33343 | 823F |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-72
577 | 33344 | 8240 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1013
578 | 33345 | 8241 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
579 | 33346 | 8242
580 | 33347 | 8243 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
581 | 33348 | 8244 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
582 | 33349 | 8245 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
583 | 33350 | 8246
584 | 33351 | 8247 | 第54条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-112
585 | 33352 | 8248 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-25
586 | 33353 | 8249 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-36
587 | 33354 | 824A |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-72
588 | 33355 | 824B |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1013
589 | 33356 | 824C |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
590 | 33357 | 824D
591 | 33358 | 824E |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
592 | 33359 | 824F |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
593 | 33360 | 8250 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
594 | 33361 | 8251
595 | 33362 | 8252 | 第55条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-113
596 | 33363 | 8253 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-26
597 | 33364 | 8254 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-37
598 | 33365 | 8255 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-73
599 | 33366 | 8256 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1014
600 | 33367 | 8257 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
601 | 33368 | 8258
602 | 33369 | 8259 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
603 | 33370 | 825A |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
604 | 33371 | 825B |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
605 | 33372 | 825C
606 | 33373 | 825D | 第56条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-113
607 | 33374 | 825E |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-26
608 | 33375 | 825F |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-37
609 | 33376 | 8260 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-73
610 | 33377 | 8261 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1014
611 | 33378 | 8262 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
612 | 33379 | 8263
613 | 33380 | 8264 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
614 | 33381 | 8265 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
615 | 33382 | 8266 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
616 | 33383 | 8267
617 | 33384 | 8268 | 第57条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-113
618 | 33385 | 8269 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-26
619 | 33386 | 826A |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-37
620 | 33387 | 826B |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-73
621 | 33388 | 826C |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1014
622 | 33389 | 826D |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
623 | 33390 | 826E
624 | 33391 | 826F |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
625 | 33392 | 8270 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
626 | 33393 | 8271 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
627 | 33394 | 8272
628 | 33395 | 8273 | 第58条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-113
629 | 33396 | 8274 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-26
630 | 33397 | 8275 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-37
631 | 33398 | 8276 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-73
632 | 33399 | 8277 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1014
633 | 33400 | 8278 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
634 | 33401 | 8279
635 | 33402 | 827A |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
636 | 33403 | 827B |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
637 | 33404 | 827C |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
638 | 33405 | 827D
639 | 33406 | 827E | 第59条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-114
640 | 33407 | 827F |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-27
641 | 33408 | 8280 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-38
642 | 33409 | 8281 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-74
643 | 33410 | 8282 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1015
644 | 33411 | 8283 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
645 | 33412 | 8284
646 | 33413 | 8285 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
647 | 33414 | 8286 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
648 | 33415 | 8287 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
649 | 33416 | 8288
650 | 33417 | 8289 | 第60条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-114
651 | 33418 | 828A |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-27
652 | 33419 | 828B |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-38
653 | 33420 | 828C |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-74
654 | 33421 | 828D |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1015
655 | 33422 | 828E |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
656 | 33423 | 828F
657 | 33424 | 8290 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
658 | 33425 | 8291 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
659 | 33426 | 8292 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
660 | 33427 | 8293
661 | 33428 | 8294 | 第61条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-114 | 组别：1 成员： 0：无事件 1：传感器上上限报警 2：传感器上限报警 3：传感器下限报警 4：传感器下下限报警 5：传感器趋势报警
662 | 33429 | 8295 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-27
663 | 33430 | 8296 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-38
664 | 33431 | 8297 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-74
665 | 33432 | 8298 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1015
666 | 33433 | 8299 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
667 | 33434 | 829A
668 | 33435 | 829B |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
669 | 33436 | 829C |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
670 | 33437 | 829D |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
671 | 33438 | 829E
672 | 33439 | 829F | 第62条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-114
673 | 33440 | 82A0 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-27
674 | 33441 | 82A1 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-38
675 | 33442 | 82A2 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-74
676 | 33443 | 82A3 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1015
677 | 33444 | 82A4 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
678 | 33445 | 82A5
679 | 33446 | 82A6 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
680 | 33447 | 82A7 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
681 | 33448 | 82A8 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
682 | 33449 | 82A9
683 | 33450 | 82AA | 第63条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-115
684 | 33451 | 82AB |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-28
685 | 33452 | 82AC |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-39
686 | 33453 | 82AD |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-75
687 | 33454 | 82AE |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1016
688 | 33455 | 82AF |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
689 | 33456 | 82B0
690 | 33457 | 82B1 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
691 | 33458 | 82B2 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
692 | 33459 | 82B3 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
693 | 33460 | 82B4
694 | 33461 | 82B5 | 第64条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-115
695 | 33462 | 82B6 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-28
696 | 33463 | 82B7 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-39
697 | 33464 | 82B8 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-75
698 | 33465 | 82B9 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1016
699 | 33466 | 82BA |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
700 | 33467 | 82BB
701 | 33468 | 82BC |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
702 | 33469 | 82BD |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
703 | 33470 | 82BE |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
704 | 33471 | 82BF
705 | 33472 | 82C0 | 第65条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-115
706 | 33473 | 82C1 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-28
707 | 33474 | 82C2 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-39
708 | 33475 | 82C3 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-75
709 | 33476 | 82C4 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1016
710 | 33477 | 82C5 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
711 | 33478 | 82C6
712 | 33479 | 82C7 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
713 | 33480 | 82C8 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
714 | 33481 | 82C9 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
715 | 33482 | 82CA
716 | 33483 | 82CB | 第66条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-115
717 | 33484 | 82CC |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-28
718 | 33485 | 82CD |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-39
719 | 33486 | 82CE |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-75
720 | 33487 | 82CF |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1016
721 | 33488 | 82D0 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
722 | 33489 | 82D1
723 | 33490 | 82D2 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
724 | 33491 | 82D3 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
725 | 33492 | 82D4 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
726 | 33493 | 82D5
727 | 33494 | 82D6 | 第67条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-116
728 | 33495 | 82D7 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-29
729 | 33496 | 82D8 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-40
730 | 33497 | 82D9 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-76
731 | 33498 | 82DA |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1017
732 | 33499 | 82DB |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
733 | 33500 | 82DC
734 | 33501 | 82DD |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
735 | 33502 | 82DE |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
736 | 33503 | 82DF |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
737 | 33504 | 82E0
738 | 33505 | 82E1 | 第68条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-116
739 | 33506 | 82E2 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-29
740 | 33507 | 82E3 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-40
741 | 33508 | 82E4 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-76
742 | 33509 | 82E5 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1017
743 | 33510 | 82E6 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
744 | 33511 | 82E7
745 | 33512 | 82E8 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
746 | 33513 | 82E9 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
747 | 33514 | 82EA |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
748 | 33515 | 82EB
749 | 33516 | 82EC | 第69条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-116
750 | 33517 | 82ED |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-29
751 | 33518 | 82EE |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-40
752 | 33519 | 82EF |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-76
753 | 33520 | 82F0 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1017
754 | 33521 | 82F1 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
755 | 33522 | 82F2
756 | 33523 | 82F3 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
757 | 33524 | 82F4 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
758 | 33525 | 82F5 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
759 | 33526 | 82F6
760 | 33527 | 82F7 | 第70条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-116
761 | 33528 | 82F8 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-29
762 | 33529 | 82F9 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-40
763 | 33530 | 82FA |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-76
764 | 33531 | 82FB |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1017
765 | 33532 | 82FC |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
766 | 33533 | 82FD
767 | 33534 | 82FE |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
768 | 33535 | 82FF |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
769 | 33536 | 8300 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
770 | 33537 | 8301
771 | 33538 | 8302 | 第71条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-117
772 | 33539 | 8303 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-30
773 | 33540 | 8304 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-41
774 | 33541 | 8305 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-77
775 | 33542 | 8306 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1018
776 | 33543 | 8307 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
777 | 33544 | 8308
778 | 33545 | 8309 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
779 | 33546 | 830A |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
780 | 33547 | 830B |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
781 | 33548 | 830C
782 | 33549 | 830D | 第72条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-117
783 | 33550 | 830E |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-30
784 | 33551 | 830F |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-41
785 | 33552 | 8310 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-77
786 | 33553 | 8311 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1018
787 | 33554 | 8312 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
788 | 33555 | 8313
789 | 33556 | 8314 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
790 | 33557 | 8315 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
791 | 33558 | 8316 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
792 | 33559 | 8317
793 | 33560 | 8318 | 第73条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-117
794 | 33561 | 8319 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-30
795 | 33562 | 831A |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-41
796 | 33563 | 831B |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-77
797 | 33564 | 831C |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1018
798 | 33565 | 831D |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
799 | 33566 | 831E
800 | 33567 | 831F |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
801 | 33568 | 8320 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
802 | 33569 | 8321 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
803 | 33570 | 8322
804 | 33571 | 8323 | 第74条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-117
805 | 33572 | 8324 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-30
806 | 33573 | 8325 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-41
807 | 33574 | 8326 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-77
808 | 33575 | 8327 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1018
809 | 33576 | 8328 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
810 | 33577 | 8329
811 | 33578 | 832A |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
812 | 33579 | 832B |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
813 | 33580 | 832C |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
814 | 33581 | 832D
815 | 33582 | 832E | 第75条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-118
816 | 33583 | 832F |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-31
817 | 33584 | 8330 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-42
818 | 33585 | 8331 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-78
819 | 33586 | 8332 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1019
820 | 33587 | 8333 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
821 | 33588 | 8334
822 | 33589 | 8335 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
823 | 33590 | 8336 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
824 | 33591 | 8337 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
825 | 33592 | 8338
826 | 33593 | 8339 | 第76条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-118
827 | 33594 | 833A |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-31
828 | 33595 | 833B |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-42
829 | 33596 | 833C |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-78
830 | 33597 | 833D |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1019
831 | 33598 | 833E |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
832 | 33599 | 833F
833 | 33600 | 8340 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
834 | 33601 | 8341 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
835 | 33602 | 8342 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
836 | 33603 | 8343
837 | 33604 | 8344 | 第77条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-118
838 | 33605 | 8345 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-31
839 | 33606 | 8346 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-42
840 | 33607 | 8347 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-78
841 | 33608 | 8348 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1019
842 | 33609 | 8349 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
843 | 33610 | 834A
844 | 33611 | 834B |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
845 | 33612 | 834C |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
846 | 33613 | 834D |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
847 | 33614 | 834E
848 | 33615 | 834F | 第78条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-118
849 | 33616 | 8350 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-31
850 | 33617 | 8351 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-42
851 | 33618 | 8352 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-78
852 | 33619 | 8353 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1019
853 | 33620 | 8354 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
854 | 33621 | 8355
855 | 33622 | 8356 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
856 | 33623 | 8357 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
857 | 33624 | 8358 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
858 | 33625 | 8359
859 | 33626 | 835A | 第79条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-119
860 | 33627 | 835B |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-32
861 | 33628 | 835C |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-43
862 | 33629 | 835D |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-79
863 | 33630 | 835E |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1020
864 | 33631 | 835F |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
865 | 33632 | 8360
866 | 33633 | 8361 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
867 | 33634 | 8362 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
868 | 33635 | 8363 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
869 | 33636 | 8364
870 | 33637 | 8365 | 第80条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-119
871 | 33638 | 8366 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-32
872 | 33639 | 8367 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-43
873 | 33640 | 8368 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-79
874 | 33641 | 8369 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1020
875 | 33642 | 836A |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
876 | 33643 | 836B
877 | 33644 | 836C |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
878 | 33645 | 836D |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
879 | 33646 | 836E |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
880 | 33647 | 836F
881 | 33648 | 8370 | 第81条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-119
882 | 33649 | 8371 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-32
883 | 33650 | 8372 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-43
884 | 33651 | 8373 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-79
885 | 33652 | 8374 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1020
886 | 33653 | 8375 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
887 | 33654 | 8376
888 | 33655 | 8377 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
889 | 33656 | 8378 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
890 | 33657 | 8379 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
891 | 33658 | 837A
892 | 33659 | 837B | 第82条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-119
893 | 33660 | 837C |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-32
894 | 33661 | 837D |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-43
895 | 33662 | 837E |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-79
896 | 33663 | 837F |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1020
897 | 33664 | 8380 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
898 | 33665 | 8381
899 | 33666 | 8382 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
900 | 33667 | 8383 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
901 | 33668 | 8384 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
902 | 33669 | 8385
903 | 33670 | 8386 | 第83条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-120
904 | 33671 | 8387 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-33
905 | 33672 | 8388 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-44
906 | 33673 | 8389 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-80
907 | 33674 | 838A |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1021
908 | 33675 | 838B |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
909 | 33676 | 838C
910 | 33677 | 838D |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
911 | 33678 | 838E |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
912 | 33679 | 838F |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
913 | 33680 | 8390
914 | 33681 | 8391 | 第84条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-120
915 | 33682 | 8392 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-33
916 | 33683 | 8393 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-44
917 | 33684 | 8394 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-80
918 | 33685 | 8395 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1021
919 | 33686 | 8396 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
920 | 33687 | 8397
921 | 33688 | 8398 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
922 | 33689 | 8399 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
923 | 33690 | 839A |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
924 | 33691 | 839B
925 | 33692 | 839C | 第85条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-120
926 | 33693 | 839D |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-33
927 | 33694 | 839E |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-44
928 | 33695 | 839F |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-80
929 | 33696 | 83A0 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1021
930 | 33697 | 83A1 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
931 | 33698 | 83A2
932 | 33699 | 83A3 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
933 | 33700 | 83A4 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
934 | 33701 | 83A5 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
935 | 33702 | 83A6
936 | 33703 | 83A7 | 第86条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-120
937 | 33704 | 83A8 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-33
938 | 33705 | 83A9 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-44
939 | 33706 | 83AA |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-80
940 | 33707 | 83AB |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1021
941 | 33708 | 83AC |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
942 | 33709 | 83AD
943 | 33710 | 83AE |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
944 | 33711 | 83AF |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
945 | 33712 | 83B0 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
946 | 33713 | 83B1
947 | 33714 | 83B2 | 第87条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-121
948 | 33715 | 83B3 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-34
949 | 33716 | 83B4 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-45
950 | 33717 | 83B5 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-81
951 | 33718 | 83B6 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1022
952 | 33719 | 83B7 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
953 | 33720 | 83B8
954 | 33721 | 83B9 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
955 | 33722 | 83BA |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
956 | 33723 | 83BB |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
957 | 33724 | 83BC
958 | 33725 | 83BD | 第88条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-121
959 | 33726 | 83BE |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-34
960 | 33727 | 83BF |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-45
961 | 33728 | 83C0 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-81
962 | 33729 | 83C1 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1022
963 | 33730 | 83C2 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
964 | 33731 | 83C3
965 | 33732 | 83C4 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
966 | 33733 | 83C5 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
967 | 33734 | 83C6 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
968 | 33735 | 83C7
969 | 33736 | 83C8 | 第89条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-121
970 | 33737 | 83C9 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-34
971 | 33738 | 83CA |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-45
972 | 33739 | 83CB |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-81
973 | 33740 | 83CC |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1022
974 | 33741 | 83CD |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
975 | 33742 | 83CE
976 | 33743 | 83CF |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
977 | 33744 | 83D0 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
978 | 33745 | 83D1 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
979 | 33746 | 83D2
980 | 33747 | 83D3 | 第90条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-121
981 | 33748 | 83D4 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-34
982 | 33749 | 83D5 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-45
983 | 33750 | 83D6 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-81
984 | 33751 | 83D7 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1022
985 | 33752 | 83D8 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
986 | 33753 | 83D9
987 | 33754 | 83DA |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
988 | 33755 | 83DB |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
989 | 33756 | 83DC |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
990 | 33757 | 83DD
991 | 33758 | 83DE | 第91条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-122
992 | 33759 | 83DF |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-35
993 | 33760 | 83E0 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-46
994 | 33761 | 83E1 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-82
995 | 33762 | 83E2 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1023
996 | 33763 | 83E3 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
997 | 33764 | 83E4
998 | 33765 | 83E5 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
999 | 33766 | 83E6 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1000 | 33767 | 83E7 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1001 | 33768 | 83E8
1002 | 33769 | 83E9 | 第92条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-122
1003 | 33770 | 83EA |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-35
1004 | 33771 | 83EB |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-46
1005 | 33772 | 83EC |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-82
1006 | 33773 | 83ED |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1023
1007 | 33774 | 83EE |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1008 | 33775 | 83EF
1009 | 33776 | 83F0 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1010 | 33777 | 83F1 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1011 | 33778 | 83F2 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1012 | 33779 | 83F3
1013 | 33780 | 83F4 | 第93条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-122
1014 | 33781 | 83F5 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-35
1015 | 33782 | 83F6 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-46
1016 | 33783 | 83F7 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-82
1017 | 33784 | 83F8 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1023
1018 | 33785 | 83F9 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1019 | 33786 | 83FA
1020 | 33787 | 83FB |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1021 | 33788 | 83FC |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1022 | 33789 | 83FD |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1023 | 33790 | 83FE
1024 | 33791 | 83FF | 第94条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-122
1025 | 33792 | 8400 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-35
1026 | 33793 | 8401 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-46
1027 | 33794 | 8402 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-82
1028 | 33795 | 8403 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1023
1029 | 33796 | 8404 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1030 | 33797 | 8405
1031 | 33798 | 8406 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1032 | 33799 | 8407 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1033 | 33800 | 8408 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1034 | 33801 | 8409
1035 | 33802 | 840A | 第95条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-123
1036 | 33803 | 840B |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-36
1037 | 33804 | 840C |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-47
1038 | 33805 | 840D |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-83
1039 | 33806 | 840E |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1024
1040 | 33807 | 840F |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1041 | 33808 | 8410
1042 | 33809 | 8411 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1043 | 33810 | 8412 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1044 | 33811 | 8413 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1045 | 33812 | 8414
1046 | 33813 | 8415 | 第96条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-123
1047 | 33814 | 8416 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-36
1048 | 33815 | 8417 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-47
1049 | 33816 | 8418 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-83
1050 | 33817 | 8419 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1024
1051 | 33818 | 841A |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1052 | 33819 | 841B
1053 | 33820 | 841C |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1054 | 33821 | 841D |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1055 | 33822 | 841E |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1056 | 33823 | 841F
1057 | 33824 | 8420 | 第97条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-123
1058 | 33825 | 8421 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-36
1059 | 33826 | 8422 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-47
1060 | 33827 | 8423 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-83
1061 | 33828 | 8424 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1024
1062 | 33829 | 8425 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1063 | 33830 | 8426
1064 | 33831 | 8427 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1065 | 33832 | 8428 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1066 | 33833 | 8429 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1067 | 33834 | 842A
1068 | 33835 | 842B | 第98条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-123
1069 | 33836 | 842C |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-36
1070 | 33837 | 842D |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-47
1071 | 33838 | 842E |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-83
1072 | 33839 | 842F |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1024
1073 | 33840 | 8430 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1074 | 33841 | 8431
1075 | 33842 | 8432 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1076 | 33843 | 8433 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1077 | 33844 | 8434 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1078 | 33845 | 8435
1079 | 33846 | 8436 | 第99条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-124
1080 | 33847 | 8437 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-37
1081 | 33848 | 8438 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-48
1082 | 33849 | 8439 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-84
1083 | 33850 | 843A |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1025
1084 | 33851 | 843B |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1085 | 33852 | 843C
1086 | 33853 | 843D |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1087 | 33854 | 843E |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1088 | 33855 | 843F |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1089 | 33856 | 8440
1090 | 33857 | 8441 | 第100条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-124
1091 | 33858 | 8442 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-37
1092 | 33859 | 8443 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-48
1093 | 33860 | 8444 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-84
1094 | 33861 | 8445 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1025
1095 | 33862 | 8446 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1096 | 33863 | 8447
1097 | 33864 | 8448 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1098 | 33865 | 8449 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1099 | 33866 | 844A |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1100 | 33867 | 844B
1101 | 33868 | 844C | 第101条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-124
1102 | 33869 | 844D |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-37
1103 | 33870 | 844E |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-48
1104 | 33871 | 844F |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-84
1105 | 33872 | 8450 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1025
1106 | 33873 | 8451 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1107 | 33874 | 8452
1108 | 33875 | 8453 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1109 | 33876 | 8454 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1110 | 33877 | 8455 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1111 | 33878 | 8456
1112 | 33879 | 8457 | 第102条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-124
1113 | 33880 | 8458 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-37
1114 | 33881 | 8459 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-48
1115 | 33882 | 845A |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-84
1116 | 33883 | 845B |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1025
1117 | 33884 | 845C |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1118 | 33885 | 845D
1119 | 33886 | 845E |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1120 | 33887 | 845F |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1121 | 33888 | 8460 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1122 | 33889 | 8461
1123 | 33890 | 8462 | 第103条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-125
1124 | 33891 | 8463 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-38
1125 | 33892 | 8464 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-49
1126 | 33893 | 8465 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-85
1127 | 33894 | 8466 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1026
1128 | 33895 | 8467 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1129 | 33896 | 8468
1130 | 33897 | 8469 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1131 | 33898 | 846A |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1132 | 33899 | 846B |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1133 | 33900 | 846C
1134 | 33901 | 846D | 第104条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-125
1135 | 33902 | 846E |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-38
1136 | 33903 | 846F |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-49
1137 | 33904 | 8470 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-85
1138 | 33905 | 8471 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1026
1139 | 33906 | 8472 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1140 | 33907 | 8473
1141 | 33908 | 8474 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1142 | 33909 | 8475 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1143 | 33910 | 8476 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1144 | 33911 | 8477
1145 | 33912 | 8478 | 第105条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-125
1146 | 33913 | 8479 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-38
1147 | 33914 | 847A |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-49
1148 | 33915 | 847B |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-85
1149 | 33916 | 847C |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1026
1150 | 33917 | 847D |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1151 | 33918 | 847E
1152 | 33919 | 847F |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1153 | 33920 | 8480 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1154 | 33921 | 8481 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1155 | 33922 | 8482
1156 | 33923 | 8483 | 第106条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-125
1157 | 33924 | 8484 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-38
1158 | 33925 | 8485 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-49
1159 | 33926 | 8486 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-85
1160 | 33927 | 8487 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1026
1161 | 33928 | 8488 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1162 | 33929 | 8489
1163 | 33930 | 848A |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1164 | 33931 | 848B |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1165 | 33932 | 848C |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1166 | 33933 | 848D
1167 | 33934 | 848E | 第107条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-126
1168 | 33935 | 848F |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-39
1169 | 33936 | 8490 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-50
1170 | 33937 | 8491 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-86
1171 | 33938 | 8492 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1027
1172 | 33939 | 8493 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1173 | 33940 | 8494
1174 | 33941 | 8495 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1175 | 33942 | 8496 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1176 | 33943 | 8497 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1177 | 33944 | 8498
1178 | 33945 | 8499 | 第108条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-126
1179 | 33946 | 849A |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-39
1180 | 33947 | 849B |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-50
1181 | 33948 | 849C |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-86
1182 | 33949 | 849D |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1027
1183 | 33950 | 849E |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1184 | 33951 | 849F
1185 | 33952 | 84A0 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1186 | 33953 | 84A1 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1187 | 33954 | 84A2 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1188 | 33955 | 84A3
1189 | 33956 | 84A4 | 第109条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-100
1190 | 33957 | 84A5 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-13
1191 | 33958 | 84A6 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-24
1192 | 33959 | 84A7 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-60
1193 | 33960 | 84A8 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1001
1194 | 33961 | 84A9 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1195 | 33962 | 84AA
1196 | 33963 | 84AB |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1197 | 33964 | 84AC |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1198 | 33965 | 84AD |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1199 | 33966 | 84AE
1200 | 33967 | 84AF | 第110条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-100
1201 | 33968 | 84B0 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-13
1202 | 33969 | 84B1 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-24
1203 | 33970 | 84B2 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-60
1204 | 33971 | 84B3 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1001
1205 | 33972 | 84B4 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1206 | 33973 | 84B5
1207 | 33974 | 84B6 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1208 | 33975 | 84B7 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1209 | 33976 | 84B8 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1210 | 33977 | 84B9
1211 | 33978 | 84BA | 第111条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-101
1212 | 33979 | 84BB |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-14
1213 | 33980 | 84BC |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-25
1214 | 33981 | 84BD |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-61
1215 | 33982 | 84BE |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1002
1216 | 33983 | 84BF |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1217 | 33984 | 84C0
1218 | 33985 | 84C1 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1219 | 33986 | 84C2 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1220 | 33987 | 84C3 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1221 | 33988 | 84C4
1222 | 33989 | 84C5 | 第112条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-101
1223 | 33990 | 84C6 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-14
1224 | 33991 | 84C7 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-25
1225 | 33992 | 84C8 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-61
1226 | 33993 | 84C9 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1002
1227 | 33994 | 84CA |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1228 | 33995 | 84CB
1229 | 33996 | 84CC |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1230 | 33997 | 84CD |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1231 | 33998 | 84CE |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1232 | 33999 | 84CF
1233 | 34000 | 84D0 | 第113条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-101
1234 | 34001 | 84D1 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-14
1235 | 34002 | 84D2 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-25
1236 | 34003 | 84D3 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-61
1237 | 34004 | 84D4 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1002
1238 | 34005 | 84D5 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1239 | 34006 | 84D6
1240 | 34007 | 84D7 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1241 | 34008 | 84D8 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1242 | 34009 | 84D9 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1243 | 34010 | 84DA
1244 | 34011 | 84DB | 第114条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-101
1245 | 34012 | 84DC |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-14
1246 | 34013 | 84DD |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-25
1247 | 34014 | 84DE |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-61
1248 | 34015 | 84DF |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1002
1249 | 34016 | 84E0 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1250 | 34017 | 84E1
1251 | 34018 | 84E2 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1252 | 34019 | 84E3 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1253 | 34020 | 84E4 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1254 | 34021 | 84E5
1255 | 34022 | 84E6 | 第115条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-102
1256 | 34023 | 84E7 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-15
1257 | 34024 | 84E8 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-26
1258 | 34025 | 84E9 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-62
1259 | 34026 | 84EA |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1003
1260 | 34027 | 84EB |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1261 | 34028 | 84EC
1262 | 34029 | 84ED |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1263 | 34030 | 84EE |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1264 | 34031 | 84EF |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1265 | 34032 | 84F0
1266 | 34033 | 84F1 | 第116条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-102
1267 | 34034 | 84F2 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-15
1268 | 34035 | 84F3 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-26
1269 | 34036 | 84F4 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-62
1270 | 34037 | 84F5 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1003
1271 | 34038 | 84F6 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1272 | 34039 | 84F7
1273 | 34040 | 84F8 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1274 | 34041 | 84F9 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1275 | 34042 | 84FA |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1276 | 34043 | 84FB
1277 | 34044 | 84FC | 第117条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-102
1278 | 34045 | 84FD |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-15
1279 | 34046 | 84FE |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-26
1280 | 34047 | 84FF |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-62
1281 | 34048 | 8500 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1003
1282 | 34049 | 8501 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1283 | 34050 | 8502
1284 | 34051 | 8503 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1285 | 34052 | 8504 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1286 | 34053 | 8505 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1287 | 34054 | 8506
1288 | 34055 | 8507 | 第118条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-102
1289 | 34056 | 8508 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-15
1290 | 34057 | 8509 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-26
1291 | 34058 | 850A |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-62
1292 | 34059 | 850B |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1003
1293 | 34060 | 850C |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1294 | 34061 | 850D
1295 | 34062 | 850E |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1296 | 34063 | 850F |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1297 | 34064 | 8510 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1298 | 34065 | 8511
1299 | 34066 | 8512 | 第119条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-103
1300 | 34067 | 8513 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-16
1301 | 34068 | 8514 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-27
1302 | 34069 | 8515 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-63
1303 | 34070 | 8516 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1004
1304 | 34071 | 8517 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1305 | 34072 | 8518
1306 | 34073 | 8519 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1307 | 34074 | 851A |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1308 | 34075 | 851B |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1309 | 34076 | 851C
1310 | 34077 | 851D | 第120条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-103
1311 | 34078 | 851E |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-16
1312 | 34079 | 851F |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-27
1313 | 34080 | 8520 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-63
1314 | 34081 | 8521 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1004
1315 | 34082 | 8522 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1316 | 34083 | 8523
1317 | 34084 | 8524 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1318 | 34085 | 8525 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1319 | 34086 | 8526 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1320 | 34087 | 8527
1321 | 34088 | 8528 | 第121条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-103 | 组别：2 成员： 0：无事件 1：网关掉电
1322 | 34089 | 8529 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-16
1323 | 34090 | 852A |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-27
1324 | 34091 | 852B |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-63
1325 | 34092 | 852C |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1004
1326 | 34093 | 852D |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1327 | 34094 | 852E
1328 | 34095 | 852F |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1329 | 34096 | 8530 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1330 | 34097 | 8531 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1331 | 34098 | 8532
1332 | 34099 | 8533 | 第122条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-103
1333 | 34100 | 8534 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-16
1334 | 34101 | 8535 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-27
1335 | 34102 | 8536 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-63
1336 | 34103 | 8537 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1004
1337 | 34104 | 8538 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1338 | 34105 | 8539
1339 | 34106 | 853A |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1340 | 34107 | 853B |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1341 | 34108 | 853C |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1342 | 34109 | 853D
1343 | 34110 | 853E | 第123条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-104 | 组别：3 成员： 0：无事件 1：网关上电 2：参数更改 3：soe记录清除
1344 | 34111 | 853F |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-17
1345 | 34112 | 8540 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-28
1346 | 34113 | 8541 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-64
1347 | 34114 | 8542 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1005
1348 | 34115 | 8543 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1349 | 34116 | 8544
1350 | 34117 | 8545 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1351 | 34118 | 8546 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1352 | 34119 | 8547 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1353 | 34120 | 8548
1354 | 34121 | 8549 | 第124条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-104
1355 | 34122 | 854A |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-17
1356 | 34123 | 854B |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-28
1357 | 34124 | 854C |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-64
1358 | 34125 | 854D |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1005
1359 | 34126 | 854E |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1360 | 34127 | 854F
1361 | 34128 | 8550 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1362 | 34129 | 8551 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1363 | 34130 | 8552 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1364 | 34131 | 8553
1365 | 34132 | 8554 | 第125条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-104
1366 | 34133 | 8555 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-17
1367 | 34134 | 8556 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-28
1368 | 34135 | 8557 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-64
1369 | 34136 | 8558 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1005
1370 | 34137 | 8559 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1371 | 34138 | 855A
1372 | 34139 | 855B |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1373 | 34140 | 855C |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1374 | 34141 | 855D |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1375 | 34142 | 855E
1376 | 34143 | 855F | 第126条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-104
1377 | 34144 | 8560 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-17
1378 | 34145 | 8561 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-28
1379 | 34146 | 8562 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-64
1380 | 34147 | 8563 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1005
1381 | 34148 | 8564 |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1382 | 34149 | 8565
1383 | 34150 | 8566 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1384 | 34151 | 8567 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1385 | 34152 | 8568 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1386 | 34153 | 8569
1387 | 34154 | 856A | 第127条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-105
1388 | 34155 | 856B |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-18
1389 | 34156 | 856C |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-29
1390 | 34157 | 856D |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-65
1391 | 34158 | 856E |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1006
1392 | 34159 | 856F |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1393 | 34160 | 8570
1394 | 34161 | 8571 |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1395 | 34162 | 8572 |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1396 | 34163 | 8573 |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1397 | 34164 | 8574
1398 | 34165 | 8575 | 第128条 | Event type（group，member） | Unsigned 16 bit | 0 | high byte：0-37，low byte：0-105
1399 | 34166 | 8576 |  | occorring time(Year, month) | Unsigned 16 bit | 0 | high byte：0-99，low byte：1-18
1400 | 34167 | 8577 |  | occorring time(date, hour) | Unsigned 16 bit | 0 | high byte：1-31，low byte：0-29
1401 | 34168 | 8578 |  | occorring time(minute, second) | Unsigned 16 bit | 0 | high byte：0-59，low byte：0-65
1402 | 34169 | 8579 |  | occorring time(millisecond) | Unsigned 16 bit | 0 | 0-1006
1403 | 34170 | 857A |  | Slave Sensor ID | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1404 | 34171 | 857B
1405 | 34172 | 857C |  | alarm value | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1406 | 34173 | 857D |  | alarm limited value(last alarm value) | Unsigned 16 bit | 0 | 0~0xFFFFFFFF
1407 | 34174 | 857E |  | Location flag | Unsigned 32 bit | 0 | 0~0xFFFFFFFF
1408 | 34175 | 857F

## CDXX（work mode setting）
Work Mode(function code 10 write)
No. | address Decimal | address Hexadecimal | Name | Default Value | Value Range
1 | 52480 | CD00 | Low bit of password | 1234 | 1234
2 | 52481 | CD01 | High bit of password | 1234 | 1234
Example: Receiver address is 01 command: 01 10 CD 00 00 02 04 12 34 12 34 CRCL CRCH meaning: save the connetced current Slave Sensor information to holding register, and set the receiver work mode from Aotumatic Mode to Manual Mode.

## CEXX(Factory Reset)
Fatory Reset(function code 10 write)
No. | address Decimal | address Hexadecimal | Name | Default Value | Value Range
1 | 52896 | CEA0 | Low bit of password | 1234 | 1234
2 | 52897 | CEA1 | High bit of password | 7799 | 7799
Example: Receiver address is 01 command: 01 10 CE A0 00 02 04 12 34 77 99 CRCL CRCH Meaning: Fatory reset(except for the unique identifier and domain name password)

## F0XX(Alarm reset)
Alarm reset(Function Code 06)
No. | address Decimal | address Hexadecimal | Name | Default Value | Value Range
1 | 61440 | F000 | Alarm reset | 0 | 0-1

## CXXX区 (hidden)
校表参数区(不对外公开)
| 地址 (10进制) | 地址 (16进制) | 类别 | 参数名称 | 默认值 | 取值范围
1 | 52224 | CC00 | 校 表 参 数 | A相电压校表参数 | 0 | -32768～32767
2 | 52225 | CC01 |  | B相电压校表参数 | 0 | -32768～32767
3 | 52226 | CC02 |  | C相电压校表参数 | 0 | -32768～32767
4 | 52227 | CC03 |  | A相电流校表参数 | 0 | -32768～32767
5 | 52228 | CC04 |  | B相电流校表参数 | 0 | -32768～32767
6 | 52229 | CC05 |  | C相电流校表参数 | 0 | -32768～32767
7 | 52230 | CC06 |  | A相相角校表参数 | 0 | -36000～36000
8 | 52231 | CC07 |  | B相相角校表参数 | 0 | -36000～36000
9 | 52232 | CC08 |  | C相相角校表参数 | 0 | -36000～36000
读取校表参数区(不对外公开)03读
| 地址 (10进制) | 地址 (16进制) | 类别 | 参数名称 | 默认值 | 取值范围
| 52224 | CC00 | 校 表 参 数 | A相电压校表参数 | 0 | -32768～32767
| 52225 | CC01 |  | B相电压校表参数 | 0 | -32768～32767
| 52226 | CC02 |  | C相电压校表参数 | 0 | -32768～32767
| 52227 | CC03 |  | A相电流校表参数 | 0 | -32768～32767
| 52228 | CC04 |  | B相电流校表参数 | 0 | -32768～32767
| 52229 | CC05 |  | C相电流校表参数 | 0 | -32768～32767
| 52230 | CC06 |  | A相相角校表参数 | 0 | -36000～36000
| 52231 | CC07 |  | B相相角校表参数 | 0 | -36000～36000
| 52232 | CC08 |  | C相相角校表参数 | 0 | -36000～36000
校表密码(不对外公开)
1 | 52480 | CD00 | 校表 密码 | 校表密码高位 | 1111H | 不可更改
2 | 52481 | CD01 |  | 校表密码低位 | 2222H
清校表密码(不对外公开)
1 | 52480 | CD00 | 校表 密码 | 校表密码高位 | 3333H | 不可更改
2 | 52481 | CD01 |  | 校表密码低位 | 4444H
恢复出厂设置密码(不对外公开)
1 | 52896 | CEA0 | 恢复密码 | 校表密码高位 | 1234H | 不可更改
2 | 52896 | CEA0 |  | 校表密码低位 | 7799H
电能表底码清零密码(不对外公开)
1 | 52992 | CF00 | 底码 清零 | 校表密码高位 | 5555H | 不可更改
2 | 52993 | CF01 |  | 校表密码低位 | 6666H
扩展选型(不对外公开)
1 | 51712 | CA00 | 扩展选型 | 高位 | 000BH（默认） | 0：DI 1：DO 2: 电能表 3： 全功能表 置1代表选中
2 | 51713 | CA01 |  | 低位 | 007fH（默认） | 备注：由低到高:DI 4位，DO 2位
软件硬件版本号(不对外公开)
1 | 51712 | D000 | 版本号 | 高位 | xxxxH | 低位：软件版本号；高位：硬件版本号
2 | 51713 | D001 |  | 低位 | xxxxH
实时电度区写底码（不对外公开）
| 地址 (10进制) | 地址 (16进制) | 类别 | 参数名称 | 出厂值 | 取值范围
| 16384 | 4000 | 总实时电度 | 总有功电能 | 0 | 0～99999999.9
| 16385 | 4001
| 16386 | 4002 |  | 正向有功电能 | 0 | 0～99999999.9
| 16387 | 4003
| 16388 | 4004 |  | 反向有功电能 | 0 | 0～99999999.9
| 16389 | 4005
| 16390 | 4006 |  | 总无功电度 | 0 | 0～99999999.9
| 16391 | 4007
| 16392 | 4008 |  | 正向无功电度 | 0 | 0～99999999.9
| 16393 | 4009
| 16394 | 400A |  | 反向无功电度 | 0 | 0～99999999.9
| 16395 | 400B
写当前月复费率历史电度底码（不对外公开）
| 地址 (10进制) | 地址 (16进制) | 类别 | 参数名称 | 参数名称 | 出厂值 | 取值范围
| 52512 | CD20 | 当前月电能 | 总电度 | 总有功电能 | 0 | 0～99999999.9
| 52513 | CD21
| 52514 | CD22 |  |  | 正向有功电能
| 52515 | CD23
| 52516 | CD24 |  |  | 反向有功电能
| 52517 | CD25
| 52518 | CD26 |  |  | 总无功电度
| 52519 | CD27
| 52520 | CD28 |  |  | 正向无功电度
| 52521 | CD29
| 52522 | CD2A |  |  | 反向无功电度
| 52523 | CD2B
| 52524 | CD2C |  | 尖时电度 | 总有功电能 | 0 | 0～99999999.9
| 52525 | CD2D
| 52526 | CD2E |  |  | 正向有功电能
| 52527 | CD2F
| 52528 | CD30 |  |  | 反向有功电能
| 52529 | CD31
| 52530 | CD32 |  |  | 总无功电度
| 52531 | CD33
| 52532 | CD34 |  |  | 正向无功电度
| 52533 | CD35
| 52534 | CD36 |  |  | 反向无功电度
| 52535 | CD37
| 52536 | CD38 |  | 峰时电度 | 总有功电能 | 0 | 0～99999999.9
| 52537 | CD39
| 52538 | CD3A |  |  | 正向有功电能
| 52539 | CD3B
| 52540 | CD3C |  |  | 反向有功电能
| 52541 | CD3D
| 52542 | CD3E |  |  | 总无功电度
| 52543 | CD3F
| 52544 | CD40 |  |  | 正向无功电度
| 52545 | CD41
| 52546 | CD42 |  |  | 反向无功电度
| 52547 | CD43
| 52548 | CD44 |  | 平时电度 | 总有功电能 | 0 | 0～99999999.9
| 52549 | CD45
| 52550 | CD46 |  |  | 正向有功电能
| 52551 | CD47
| 52552 | CD48 |  |  | 反向有功电能
| 52553 | CD49
| 52554 | CD4A |  |  | 总无功电度
| 52555 | CD4B
| 52556 | CD4C |  |  | 正向无功电度
| 52557 | CD4D
| 52558 | CD4E |  |  | 反向无功电度
| 52559 | CD4F
| 52560 | CD50 |  | 谷时电度 | 总有功电能 | 0 | 0～99999999.9
| 52561 | CD51
| 52562 | CD52 |  |  | 正向有功电能
| 52563 | CD53
| 52564 | CD54 |  |  | 反向有功电能
| 52565 | CD55
| 52566 | CD56 |  |  | 总无功电度
| 52567 | CD57
| 52568 | CD58 |  |  | 正向无功电度
| 52569 | CD59
| 52570 | CD5A |  |  | 反向无功电度
| 52571 | CD5B