## DI DO
DI Zone（Function Code 02 Read）--4-Channel DI (Digital Input)
| Address (Decimal) | Address (Hexadecimal) | Function Code | Register Type | Category | Parameter | Default | Value Range
1 | 0 | 0000 | 0x02 | Read-only | DI | DI1 | -- | 0～1
2 | 1 | 0001 | 0x02 | Read-only |  | DI2 | -- | 0～1
3 | 2 | 0002 | 0x02 | Read-only |  | DI3 | -- | 0～1
4 | 3 | 0003 | 0x02 | Read-only |  | DI4 | -- | 0～1
Remark： 1.The function code 02 can read the DI status, and the return value is 1 byte. Each bit stands for one DI status. E.g. if reading the data of registers 0x0000～0x0003, it will get a return value 0x05, which means that DI1, DI3 are connected，DI2, DI4 are disconnected.
DO Zone（Function Code 05 Control, 01 Read）--2-Channel DO (Digital Output)
| Address (Decimal) | Address (Hexadecimal) | Function Code | Register Type | Category | Parameter | Default | Value Range
1 | 20480 | 5000 | 05/01 | Write/Read | DO | Relay 1 | -- | Write:ff00/0000 Read：0～0x0f
2 | 20481 | 5001 | 05/01 | Write/Read |  | Relay 2 | --
Remark： 1.When the use of relay is set as remote control, the registers of this zone can be operated. If the relay working mode is set as electrical level mode, the relay will follow the action after the control command is executed; If the relay working mode is set as pulse mode, the relay will automatically change to be disconnected after a period when control command of connection is executed. And the connection time is programmable. 2.The relay application selection, working mode selection, pulse time and other related settings refer to introduction of related registers in 0x2000 area . 3.Function code 05 is used for output control(only single coil). If the control relay is connected, it will be written ff00 while if the If the control relay is disconnected, it will be written 0000. 4.Function code 01 is used for reading the status of coil and the return value is 1 byte. Each bit stands for status of one coil.E.g. if reading the data of registers 0x5000～0x5003, it will get a return value 0x0A, which means that D02, DO4 are connected，DO1, DO3 are disconnected.

## Zone 1XXX
Basic Parameters Measured Zone（Function Code 03/04 Read）
| Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
1 | 4096 | 1000 | Phase Voltage | phase A voltage | magnifying 100 times | 0～65535
2 | 4097 | 1001 |  | phase B voltage | magnifying 100 times | 0～65535
3 | 4098 | 1002 |  | phase C voltage | magnifying 100 times | 0～65535
4 | 4099 | 1003 |  | phase voltage mean value | magnifying 100 times | 0～65535
5 | 4100 | 1004 |  | zero sequence voltage | magnifying 100 times | 0～65535
6 | 4101 | 1005 | Line Voltage | line voltage(A-B) | magnifying 100 times | 0～65535
7 | 4102 | 1006 |  | line voltage(B-C) | magnifying 100 times | 0～65535
8 | 4103 | 1007 |  | line voltage(C-A) | magnifying 100 times | 0～65535
9 | 4104 | 1008 |  | line voltage mean value | magnifying 100 times | 0～65535
10 | 4105 | 1009 | Current | phase/line Current of phase A | magnifying 1,000 times | 0～65535
11 | 4106 | 100A |  | phase/line Current of phase B | magnifying 1,000 times | 0～65535
12 | 4107 | 100B |  | phase/line Current of phase C | magnifying 1,000 times | 0～65535
13 | 4108 | 100C |  | phase/line Current mean value | magnifying 1,000 times | 0～65535
14 | 4109 | 100D |  | zero sequence current | magnifying 1,000 times | 0～65535
15 | 4110 | 100E | Active Power | active power of phase A | magnifying 1,000 times | -32768～32767
16 | 4111 | 100F |  | active power of phase B | magnifying 1,000 times | -32768～32767
17 | 4112 | 1010 |  | active power of phase C | magnifying 1,000 times | -32768～32767
18 | 4113 | 1011 |  | total three-phase active power | magnifying 1,000 times | -32768～32767
19 | 4114 | 1012 | Reactive Power | reactive power of phase A | magnifying 1,000 times | -32768～32767
20 | 4115 | 1013 |  | reactive power of phase B | magnifying 1,000 times | -32768～32767
21 | 4116 | 1014 |  | reactive power of phase C | magnifying 1,000 times | -32768～32767
22 | 4117 | 1015 |  | total three-phase reactive power | magnifying 1,000 times | -32768～32767
23 | 4118 | 1016 | Apparent Power | apparent power of phase A | magnifying 1,000 times | -32768～32767
24 | 4119 | 1017 |  | apparent power of phase B | magnifying 1,000 times | -32768～32767
25 | 4120 | 1018 |  | apparent power of phase C | magnifying 1,000 times | -32768～32767
26 | 4121 | 1019 |  | total three-phase apparent power | magnifying 1,000 times | -32768～32767
27 | 4122 | 101A | Power Factor | power factor of phase A | magnifying 100 times | -100～100
28 | 4123 | 101B |  | power factor of phase B | magnifying 100 times | -100～100
29 | 4124 | 101C |  | power factor of phase C | magnifying 100 times | -100～100
30 | 4125 | 101D |  | total three-phase power factor | magnifying 100 times | -100～100
31 | 4126 | 101E | Frequency | frequency | magnifying 100 times | 0～65535
32 | 4127 | 101F | Unbalance Factor | voltage unbalance factor | magnifying 10,000 times | 0～100
33 | 4128 | 1020 |  | current unbalance factor | magnifying 10,000 times | 0～100
34 | 4129 | 1021 | Load Property | Inductance-Capacitance-Resistance （L/C/R） | -- | 76/67/82
Harmonic Parameter Zone（Function Code 03/04 Read）
| Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
1 | 4352 | 1100 | Total Harmonic Distortion Rate (THD) | line/phase voltage THD of phase A | Rx/1000×100% | 0～10000
2 | 4353 | 1101 |  | line/phase voltage THD of phase B | Rx/1000×100% | 0～10000
3 | 4354 | 1102 |  | line/phase voltage THD of phase C | Rx/1000×100% | 0～10000
4 | 4355 | 1103 |  | line/phase voltage mean value THD | Rx/1000×100% | 0～10000
5 | 4356 | 1104 |  | current THD of phase A | Rx/1000×100% | 0～10000
6 | 4357 | 1105 |  | current THD of phase B | Rx/1000×100% | 0～10000
7 | 4358 | 1106 |  | current THD of phase C | Rx/1000×100% | 0～10000
8 | 4359 | 1107 |  | current mean value THD | Rx/1000×100% | 0～10000
9 | 4360 | 1108 | (Odd) Phase A Voltage Harmonic Content | 3rd line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
10 | 4361 | 1109 |  | 5th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
11 | 4362 | 110A |  | 7th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
12 | 4363 | 110B |  | 9th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
13 | 4364 | 110C |  | 11th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
14 | 4365 | 110D |  | 13th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
15 | 4366 | 110E |  | 15th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
16 | 4367 | 110F |  | 17th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
17 | 4368 | 1110 |  | 19th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
18 | 4369 | 1111 |  | 21st line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
19 | 4370 | 1112 |  | 23rd line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
20 | 4371 | 1113 |  | 25th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
21 | 4372 | 1114 |  | 27th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
22 | 4373 | 1115 |  | 29th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
23 | 4374 | 1116 |  | 31st line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
24 | 4375 | 1117 | (Even) Phase A Voltage Harmonic Content | 2nd line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
25 | 4376 | 1118 |  | 4th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
26 | 4377 | 1119 |  | 6th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
27 | 4378 | 111A |  | 8th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
28 | 4379 | 111B |  | 10th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
29 | 4380 | 111C |  | 12th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
30 | 4381 | 111D |  | 14th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
31 | 4382 | 111E |  | 16th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
32 | 4383 | 111F |  | 18th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
33 | 4384 | 1120 |  | 20th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
34 | 4385 | 1121 |  | 22nd line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
35 | 4386 | 1122 |  | 24th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
36 | 4387 | 1123 |  | 26th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
37 | 4388 | 1124 |  | 28th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
38 | 4389 | 1125 |  | 30th line/phase voltage harmonic content of Phase A | Rx/1000×100% | 0～10000
39 | 4390 | 1126 | Phase A Voltage Harmonic Analysis | odd line/phase voltage harmonic distortion rate of Phase A | Rx/1000×100% | 0～10000
40 | 4391 | 1127 |  | even line/phase voltage harmonic distortion rate of Phase A | Rx/1000×100% | 0～10000
41 | 4392 | 1128 |  | line/phase voltage crest factor of Phase A | Rx/1000×100% | 0～10000
42 | 4393 | 1129 |  | reserved |  | 0～10000
43 | 4394 | 112A | Phase B Voltage(Odd) Harmonic Content | 3rd line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
44 | 4395 | 112B |  | 5th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
45 | 4396 | 112C |  | 7th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
46 | 4397 | 112D |  | 9th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
47 | 4398 | 112E |  | 11th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
48 | 4399 | 112F |  | 13th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
49 | 4400 | 1130 |  | 15th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
50 | 4401 | 1131 |  | 17th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
51 | 4402 | 1132 |  | 19th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
52 | 4403 | 1133 |  | 21st line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
53 | 4404 | 1134 |  | 23rd line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
54 | 4405 | 1135 |  | 25th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
55 | 4406 | 1136 |  | 27th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
56 | 4407 | 1137 |  | 29th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
57 | 4408 | 1138 |  | 31st line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
58 | 4409 | 1139 | (Even) Phase B Voltage Harmonic Content | 2nd line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
59 | 4410 | 113A |  | 4th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
60 | 4411 | 113B |  | 6th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
61 | 4412 | 113C |  | 8th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
62 | 4413 | 113D |  | 10th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
63 | 4414 | 113E |  | 12th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
64 | 4415 | 113F |  | 14th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
65 | 4416 | 1140 |  | 16th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
66 | 4417 | 1141 |  | 18th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
67 | 4418 | 1142 |  | 20th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
68 | 4419 | 1143 |  | 22nd line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
69 | 4420 | 1144 |  | 24th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
70 | 4421 | 1145 |  | 26th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
71 | 4422 | 1146 |  | 28th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
72 | 4423 | 1147 |  | 30th line/phase voltage harmonic content of Phase B | Rx/1000×100% | 0～10000
73 | 4424 | 1148 | Phase B Voltage Harmonic Analysis | odd line/phase voltage harmonic distortion rate of Phase B | Rx/1000×100% | 0～10000
74 | 4425 | 1149 |  | even line/phase voltage harmonic distortion rate of Phase B | Rx/1000×100% | 0～10000
75 | 4426 | 114A |  | line/phase voltage crest factor of Phase A | Rx/1000×100% | 0～10000
76 | 4427 | 114B |  | reserved |  | 0～10000
77 | 4428 | 114C | (Odd) Phase C Voltage Harmonic Content | 3rd line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
78 | 4429 | 114D |  | 5th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
79 | 4430 | 114E |  | 7th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
80 | 4431 | 114F |  | 9th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
81 | 4432 | 1150 |  | 11th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
82 | 4433 | 1151 |  | 13th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
83 | 4434 | 1152 |  | 15th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
84 | 4435 | 1153 |  | 17th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
85 | 4436 | 1154 |  | 19th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
86 | 4437 | 1155 |  | 21st line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
87 | 4438 | 1156 |  | 23rd line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
88 | 4439 | 1157 |  | 25th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
89 | 4440 | 1158 |  | 27th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
90 | 4441 | 1159 |  | 29th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
91 | 4442 | 115A |  | 31st line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
92 | 4443 | 115B | (Even) Phase C Voltage Harmonic Content | 2nd line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
93 | 4444 | 115C |  | 4th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
94 | 4445 | 115D |  | 6th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
95 | 4446 | 115E |  | 8th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
96 | 4447 | 115F |  | 10th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
97 | 4448 | 1160 |  | 12th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
98 | 4449 | 1161 |  | 14th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
99 | 4450 | 1162 |  | 16th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
100 | 4451 | 1163 |  | 18th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
101 | 4452 | 1164 |  | 20th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
102 | 4453 | 1165 |  | 22nd line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
103 | 4454 | 1166 |  | 24th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
104 | 4455 | 1167 |  | 26th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
105 | 4456 | 1168 |  | 28th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
106 | 4457 | 1169 |  | 30th line/phase voltage harmonic content of Phase C | Rx/1000×100% | 0～10000
107 | 4458 | 116A | Phase C Voltage Harmonic Analysis | odd line/phase voltage harmonic distortion rate of Phase C | Rx/1000×100% | 0～10000
108 | 4459 | 116B |  | even line/phase voltage harmonic distortion rate of Phase C | Rx/1000×100% | 0～10000
109 | 4460 | 116C |  | line/phase voltage crest factor of Phase C | Rx/1000×100% | 0～10000
110 | 4461 | 116D |  | reserved |  | 0～10000
111 | 4462 | 116E | (Odd) Phase A Current Harmonic Content | 3rd current harmonic content of Phase A | Rx/1000×100% | 0～10000
112 | 4463 | 116F |  | 5th current harmonic content of Phase A | Rx/1000×100% | 0～10000
113 | 4464 | 1170 |  | 7th current harmonic content of Phase A | Rx/1000×100% | 0～10000
114 | 4465 | 1171 |  | 9th current harmonic content of Phase A | Rx/1000×100% | 0～10000
115 | 4466 | 1172 |  | 11th current harmonic content of Phase A | Rx/1000×100% | 0～10000
116 | 4467 | 1173 |  | 13th current harmonic content of Phase A | Rx/1000×100% | 0～10000
117 | 4468 | 1174 |  | 15th current harmonic content of Phase A | Rx/1000×100% | 0～10000
118 | 4469 | 1175 |  | 17th current harmonic content of Phase A | Rx/1000×100% | 0～10000
119 | 4470 | 1176 |  | 19th current harmonic content of Phase A | Rx/1000×100% | 0～10000
120 | 4471 | 1177 |  | 21st current harmonic content of Phase A | Rx/1000×100% | 0～10000
121 | 4472 | 1178 |  | 23rd current harmonic content of Phase A | Rx/1000×100% | 0～10000
122 | 4473 | 1179 |  | 25th current harmonic content of Phase A | Rx/1000×100% | 0～10000
123 | 4474 | 117A |  | 27th current harmonic content of Phase A | Rx/1000×100% | 0～10000
124 | 4475 | 117B |  | 29th current harmonic content of Phase A | Rx/1000×100% | 0～10000
125 | 4476 | 117C |  | 31st current harmonic content of Phase A | Rx/1000×100% | 0～10000
126 | 4477 | 117D | (Even) Phase A Current Harmonic Content | 2nd current harmonic content of Phase A | Rx/1000×100% | 0～10000
127 | 4478 | 117E |  | 4th current harmonic content of Phase A | Rx/1000×100% | 0～10000
128 | 4479 | 117F |  | 6th current harmonic content of Phase A | Rx/1000×100% | 0～10000
129 | 4480 | 1180 |  | 8th current harmonic content of Phase A | Rx/1000×100% | 0～10000
130 | 4481 | 1181 |  | 10th current harmonic content of Phase A | Rx/1000×100% | 0～10000
131 | 4482 | 1182 |  | 12th current harmonic content of Phase A | Rx/1000×100% | 0～10000
132 | 4483 | 1183 |  | 14th current harmonic content of Phase A | Rx/1000×100% | 0～10000
133 | 4484 | 1184 |  | 16th current harmonic content of Phase A | Rx/1000×100% | 0～10000
134 | 4485 | 1185 |  | 18th current harmonic content of Phase A | Rx/1000×100% | 0～10000
135 | 4486 | 1186 |  | 20th current harmonic content of Phase A | Rx/1000×100% | 0～10000
136 | 4487 | 1187 |  | 22nd current harmonic content of Phase A | Rx/1000×100% | 0～10000
137 | 4488 | 1188 |  | 24th current harmonic content of Phase A | Rx/1000×100% | 0～10000
138 | 4489 | 1189 |  | 26th current harmonic content of Phase A | Rx/1000×100% | 0～10000
139 | 4490 | 118A |  | 28th current harmonic content of Phase A | Rx/1000×100% | 0～10000
140 | 4491 | 118B |  | 30th current harmonic content of Phase A | Rx/1000×100% | 0～10000
141 | 4492 | 118C | Phase A Current Harmonic Analysis | odd current harmonic distortion rate of Phase A | Rx/1000×100% | 0～10000
142 | 4493 | 118D |  | even current harmonic distortion rate of Phase A | Rx/1000×100% | 0～10000
143 | 4494 | 118E |  | reserved |  | 0～10000
144 | 4495 | 118F | (Odd) Phase B Current Harmonic Content | 3rd current harmonic content of Phase B | Rx/1000×100% | 0～10000
145 | 4496 | 1190 |  | 5th current harmonic content of Phase B | Rx/1000×100% | 0～10000
146 | 4497 | 1191 |  | 7th current harmonic content of Phase B | Rx/1000×100% | 0～10000
147 | 4498 | 1192 |  | 9th current harmonic content of Phase B | Rx/1000×100% | 0～10000
148 | 4499 | 1193 |  | 11th current harmonic content of Phase B | Rx/1000×100% | 0～10000
149 | 4500 | 1194 |  | 13th current harmonic content of Phase B | Rx/1000×100% | 0～10000
150 | 4501 | 1195 |  | 15th current harmonic content of Phase B | Rx/1000×100% | 0～10000
151 | 4502 | 1196 |  | 17th current harmonic content of Phase B | Rx/1000×100% | 0～10000
152 | 4503 | 1197 |  | 19th current harmonic content of Phase B | Rx/1000×100% | 0～10000
153 | 4504 | 1198 |  | 21st current harmonic content of Phase B | Rx/1000×100% | 0～10000
154 | 4505 | 1199 |  | 23rd current harmonic content of Phase B | Rx/1000×100% | 0～10000
155 | 4506 | 119A |  | 25th current harmonic content of Phase B | Rx/1000×100% | 0～10000
156 | 4507 | 119B |  | 27th current harmonic content of Phase B | Rx/1000×100% | 0～10000
157 | 4508 | 119C |  | 29th current harmonic content of Phase B | Rx/1000×100% | 0～10000
158 | 4509 | 119D |  | 31st current harmonic content of Phase B | Rx/1000×100% | 0～10000
159 | 4510 | 119E | (Even) Phase B Current Harmonic Content | 2nd current harmonic content of Phase B | Rx/1000×100% | 0～10000
160 | 4511 | 119F |  | 4th current harmonic content of Phase B | Rx/1000×100% | 0～10000
161 | 4512 | 11A0 |  | 6th current harmonic content of Phase B | Rx/1000×100% | 0～10000
162 | 4513 | 11A1 |  | 8th current harmonic content of Phase B | Rx/1000×100% | 0～10000
163 | 4514 | 11A2 |  | 10th current harmonic content of Phase B | Rx/1000×100% | 0～10000
164 | 4515 | 11A3 |  | 12th current harmonic content of Phase B | Rx/1000×100% | 0～10000
165 | 4516 | 11A4 |  | 14th current harmonic content of Phase B | Rx/1000×100% | 0～10000
166 | 4517 | 11A5 |  | 16th current harmonic content of Phase B | Rx/1000×100% | 0～10000
167 | 4518 | 11A6 |  | 18th current harmonic content of Phase B | Rx/1000×100% | 0～10000
168 | 4519 | 11A7 |  | 20th current harmonic content of Phase B | Rx/1000×100% | 0～10000
169 | 4520 | 11A8 |  | 22nd current harmonic content of Phase B | Rx/1000×100% | 0～10000
170 | 4521 | 11A9 |  | 24th current harmonic content of Phase B | Rx/1000×100% | 0～10000
171 | 4522 | 11AA |  | 26th current harmonic content of Phase B | Rx/1000×100% | 0～10000
172 | 4523 | 11AB |  | 28th current harmonic content of Phase B | Rx/1000×100% | 0～10000
173 | 4524 | 11AC |  | 30th current harmonic content of Phase B | Rx/1000×100% | 0～10000
174 | 4525 | 11AD | Phase B Current Harmonic Analysis | odd current harmonic distortion rate of Phase B | Rx/1000×100% | 0～10000
175 | 4526 | 11AE |  | even current harmonic distortion rate of Phase B | Rx/1000×100% | 0～10000
176 | 4527 | 11AF |  | reserved |  | 0～10000
177 | 4528 | 11B0 | (Odd) Phase C Current Harmonic Content | 3rd current harmonic content of Phase C | Rx/1000×100% | 0～10000
178 | 4529 | 11B1 |  | 5th current harmonic content of Phase C | Rx/1000×100% | 0～10000
179 | 4530 | 11B2 |  | 7th current harmonic content of Phase C | Rx/1000×100% | 0～10000
180 | 4531 | 11B3 |  | 9th current harmonic content of Phase C | Rx/1000×100% | 0～10000
181 | 4532 | 11B4 |  | 11th current harmonic content of Phase C | Rx/1000×100% | 0～10000
182 | 4533 | 11B5 |  | 13th current harmonic content of Phase C | Rx/1000×100% | 0～10000
183 | 4534 | 11B6 |  | 15th current harmonic content of Phase C | Rx/1000×100% | 0～10000
184 | 4535 | 11B7 |  | 17th current harmonic content of Phase C | Rx/1000×100% | 0～10000
185 | 4536 | 11B8 |  | 19th current harmonic content of Phase C | Rx/1000×100% | 0～10000
186 | 4537 | 11B9 |  | 21st current harmonic content of Phase C | Rx/1000×100% | 0～10000
187 | 4538 | 11BA |  | 23rd current harmonic content of Phase C | Rx/1000×100% | 0～10000
188 | 4539 | 11BB |  | 25th current harmonic content of Phase C | Rx/1000×100% | 0～10000
189 | 4540 | 11BC |  | 27th current harmonic content of Phase C | Rx/1000×100% | 0～10000
190 | 4541 | 11BD |  | 29th current harmonic content of Phase C | Rx/1000×100% | 0～10000
191 | 4542 | 11BE |  | 31st current harmonic content of Phase C | Rx/1000×100% | 0～10000
192 | 4543 | 11BF | (Even) Phase C Current Harmonic Content | 2nd current harmonic content of Phase C | Rx/1000×100% | 0～10000
193 | 4544 | 11C0 |  | 4th current harmonic content of Phase C | Rx/1000×100% | 0～10000
194 | 4545 | 11C1 |  | 6th current harmonic content of Phase C | Rx/1000×100% | 0～10000
195 | 4546 | 11C2 |  | 8th current harmonic content of Phase C | Rx/1000×100% | 0～10000
196 | 4547 | 11C3 |  | 10th current harmonic content of Phase C | Rx/1000×100% | 0～10000
197 | 4548 | 11C4 |  | 12th current harmonic content of Phase C | Rx/1000×100% | 0～10000
198 | 4549 | 11C5 |  | 14th current harmonic content of Phase C | Rx/1000×100% | 0～10000
199 | 4550 | 11C6 |  | 16th current harmonic content of Phase C | Rx/1000×100% | 0～10000
200 | 4551 | 11C7 |  | 18th current harmonic content of Phase C | Rx/1000×100% | 0～10000
201 | 4552 | 11C8 |  | 20th current harmonic content of Phase C | Rx/1000×100% | 0～10000
202 | 4553 | 11C9 |  | 22nd current harmonic content of Phase C | Rx/1000×100% | 0～10000
203 | 4554 | 11CA |  | 24th current harmonic content of Phase C | Rx/1000×100% | 0～10000
204 | 4555 | 11CB |  | 26th current harmonic content of Phase C | Rx/1000×100% | 0～10000
205 | 4556 | 11CC |  | 28th current harmonic content of Phase C | Rx/1000×100% | 0～10000
206 | 4557 | 11CD |  | 30th current harmonic content of Phase C | Rx/1000×100% | 0～10000
207 | 4558 | 11CE | Phase C Current Harmonic Analysis | odd current harmonic distortion rate of Phase C | Rx/1000×100% | 0～10000
208 | 4559 | 11CF |  | even current harmonic distortion rate of Phase C | Rx/1000×100% | 0～10000
209 | 4560 | 11D0 |  | reserved
Remark： 1. The registers, named as "Reserved", in the harmonic parameter zone, have no function in this meter. And the data read from these registers can not be used for any reference, and theses registers are only reserved for future extended functions. 2. All the data of registers from 0x1100 to 0x11D0 need to be magnified 1000 times.

## Zone 2XXX
Basic Parameters Measured Zone（Function Code 06/0x10 Write; Function Code 03/04 Read）
No. | Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
1 | 8192 | 2000 | Basic Parameters | password protection (protection of basic parameters) | 0 | 0～9999
2 | 8193 | 2001 |  | meter communication address | 1 | 1～247
3 | 8194 | 2002 |  | RS485 serial port parameter （high byte is parity check; low byte is baud rate） | 3 | High：0:(N,8,1)，1:(E,8,1)，2:(O,8,1) Low：0:9600, 1:2400, 2:4800, 3:9600，4:19200
4 | 8195 | 2003 |  | voltage wiring mode | 0 | 0：3LN，1：2LN，2：2LL
5 | 8196 | 2004 |  | current wiring mode | 0 | 0：3CT，1：2CT，2：1CT
6 | 8197 | 2005 |  | PT | 1 | 1∼9999 Remark 1
7 | 8198 | 2006 |  | CT | 1 | 1～9999 Remark 1
8 | 8199 | 2007 |  | shift between primary energy and secondary energy | 0 | 0：secondary Energy，1：primary Energy
11 | 8202 | 200A |  | Selection of Pulse Energy Output Through DO1 Port | 1 | 0: Overcurrent alarm pulse 1：Import Active Energy, 2：Export Active Energy 3：Import Reactive Energy，4：Export Reactive Energy 5：Absolute Value & Active Energy，6：Absolute Value & Reactive Energy 7：Net Active Energy，8：Net Reactive Energy 9：Apparent Energy
12 | 8203 | 200B |  | Selection of Pulse Energy Output Through DO2 Port | 2 | 0: Trend of Current/ Vlotage Record 1：Import Active Energy, 2：Export Active Energy 3：Import Reactive Energy，4：Export Reactive Energy 5：Absolute Value & Active Energy，6：Absolute Value & Reactive Energy 7：Net Active Energy，8：Net Reactive Energy 9：Apparent Energy
13 | 8204 | 200C |  | energy decimal places | 1 | 0～4
14 | 8205 | 200D |  | spare | -- | 0
15 | 8206 | 200E |  | energy pulse constant | 9600 | 600～50000
16 | 8207 | 200F |  | backlight time | 100 | 0～999
17 | 8208 | 2010 | DO | DO1 Setting | 0x40c8 | bit15:function selection 0：Tele-control，1：Alarm； bit14:Working Mode Selection 0：Electrical Level，1：pulse； bit0～bit13: Pulse Width，range：50～3000ms remark 2
18 | 8209 | 2011 |  | DO2 Setting | 0x40c8
19 | 8210 | 2012 |  | DO3 Setting | 0x40c8
20 | 8211 | 2013 |  | DO4 Setting | 0x40c8
21 | 8212 | 2014 |  | spare | -- | 0
22 | 8213 | 2015 |  | spare | -- | 0
23 | 8214 | 2016 |  | spare | -- | 0
24 | 8215 | 2017 |  | spare | -- | 0
25 | 8216 | 2018 | Alarm | enable alarm function | 0 | 0：Close Alarm 1：Open Alarm
| 8217 | 2019 |  | enable alarm setting | 0 | ( 0：Reactive 1：Active ) remark 3 range（0～0xFFFF）
| 8218 | 201A |  | enable alarm flash | 0 | LCD Backlight: 0：Unflashing 1：Flashing
| 8219 | 201B |  | alarm output through DO1 | 0 | (0：Reactive 1：Active ) Remark 4 range（0～0xFFFF）
| 8220 | 201C |  | alarm output through DO2 | 0 | (0：Reactive 1：Active ) Remark 4 range（0～0xFFFF）
Remark： 1.The product of CT and PT should be less than 300,000. 2. If the purpose of the relay is set as alarm, the settings of pulse mode and pulse width will be invalid and can only be used as the level mode output. If the relay is set as the level mode, the pulse width will be invalid. 3. E.g. if the register is 0x0101（00000001 00000001B）, i.e., the alarm parameter setting of the 1st and the 9th groups can trigger the alarm function. 4. E.g. if the register of 0x201B was set as 0x01010x0101（00000001 00000001B）, i.e., the alarm parameter setting of the 1st or the 9th groups can trigger the alarm function. Besides, if the register（0x2010）use of DO1 is set as 1(alarm output),the DO1 will be connected. When the alarm recovers, the relay will be disconnected. 5. E.g. if under the DI wave recording mode, the register1（0x201D）is set as 0x0011（0001 0001B),i.e.if the status of DI1&DI3 is connected,it will start recording wave. DI2&DI4 will not record wave.
Multi-tariff Period Setting Zone（Function Code 10 Write; Function Code 03/04 Read）
No. | Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
1 | 8448 | 2100 | Multi-tariff Period Setting | Start Time of The 1st Period: Hour, Minute | 8:00 | High Byte，H:0～23 Low Byte，M:0～59
2 | 8449 | 2101 |  | End Time of The 1st Period: Hour, Minute | 11:00 | High Byte，H:0～23 Low Byte，M:0～59
3 | 8450 | 2102 |  | Tariff Rate of The 1st Period | 2 | 1：Sharp，2：Peak，3：Normal，4：Valley
4 | 8451 | 2103 |  | Start Time of The 2nd Period: Hour, Minute | 18:00 | High Byte，H:0～23 Low Byte，M:0～59
5 | 8452 | 2104 |  | End Time of The 2nd Period: Hour, Minute | 23:00 | High Byte，H:0～23 Low Byte，M:0～59
6 | 8453 | 2105 |  | Tariff Rate of The 2nd Period | 2 | 1：Sharp，2：Peak，3：Normal，4：Valley
7 | 8454 | 2106 |  | Start Time of The 3rd Period: Hour, Minute | 7:00 | High Byte，H:0～23 Low Byte，M:0～59
8 | 8455 | 2107 |  | End Time of The 3rd Period: Hour, Minute | 8:00 | High Byte，H:0～23 Low Byte，M:0～59
9 | 8456 | 2108 |  | Tariff Rate of The 3rd Period | 3 | 1：Sharp，2：Peak，3：Normal，4：Valley
10 | 8457 | 2109 |  | Start Time of The 4th Period: Hour, Minute | 11:00 | High Byte，H:0～23 Low Byte，M:0～59
11 | 8458 | 210A |  | End Time of The 4th Period: Hour, Minute | 18:00 | High Byte，H:0～23 Low Byte，M:0～59
12 | 8459 | 210B |  | Tariff Rate of The 4th Period | 3 | 1：Sharp，2：Peak，3：Normal，4：Valley
13 | 8460 | 210C |  | Start Time of The 5th Period: Hour, Minute | 23:00 | High Byte，H:0～23 Low Byte，M:0～59
14 | 8461 | 210D |  | End Time of The 5th Period: Hour, Minute | 7:00 | High Byte，H:0～23 Low Byte，M:0～59
15 | 8462 | 210E |  | Tariff Rate of The 5th Period | 4 | 1：Sharp，2：Peak，3：Normal，4：Valley
16 | 8463 | 210F |  | Start Time of The 6th Period: Hour, Minute | 0 | High Byte，H:0～23 Low Byte，M:0～59
17 | 8464 | 2110 |  | End Time of The 6th Period: Hour, Minute | 0 | High Byte，H:0～23 Low Byte，M:0～59
18 | 8465 | 2111 |  | Tariff Rate of The 6th Period | 0 | 1：Sharp，2：Peak，3：Normal，4：Valley
19 | 8466 | 2112 |  | Start Time of The 7th Period: Hour, Minute | 0 | High Byte，H:0～23 Low Byte，M:0～59
20 | 8467 | 2113 |  | End Time of The 7th Period: Hour, Minute | 0 | High Byte，H:0～23 Low Byte，M:0～59
21 | 8468 | 2114 |  | Tariff Rate of The 7th Period | 0 | 1：Sharp，2：Peak，3：Normal，4：Valley
22 | 8469 | 2115 |  | Start Time of The 8th Period: Hour, Minute | 0 | High Byte，H:0～23 Low Byte，M:0～59
23 | 8470 | 2116 |  | End Time of The 8th Period: Hour, Minute | 0 | High Byte，H:0～23 Low Byte，M:0～59
24 | 8471 | 2117 |  | Tariff Rate of The 8th Period | 0 | 1：Sharp，2：Peak，3：Normal，4：Valley
25 | 8472 | 2118 |  | Start Time of The 9th Period: Hour, Minute | 0 | High Byte，H:0～23 Low Byte，M:0～59
26 | 8473 | 2119 |  | End Time of The 9th Period: Hour, Minute | 0 | High Byte，H:0～23 Low Byte，M:0～59
27 | 8474 | 211A |  | Tariff Rate of The 9th Period | 0 | 1：Sharp，2：Peak，3：Normal，4：Valley
28 | 8475 | 211B |  | Start Time of The 10th Period: Hour, Minute | 0 | High Byte，H:0～23 Low Byte，M:0～59
29 | 8476 | 211C |  | End Time of The 10th Period: Hour, Minute | 0 | High Byte，H:0～23 Low Byte，M:0～59
30 | 8477 | 211D |  | Tariff Rate of The 10th Period | 0 | 1：Sharp，2：Peak，3：Normal，4：Valley
31 | 8478 | 211E | Meter Reading Time | Days | 1 | 1～30
32 | 8479 | 211F |  | Hour | 0 | 0～23

## Zone 3XXX
Real-time Clock Zone（（Function Code 0x10 Write; Function Code 03/04 Read）
No. | Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
1 | 12800 | 3200 | Time | Year | 2000 | 2000～2099
2 | 12801 | 3201 |  | Month | 1 | 1～12
3 | 12802 | 3202 |  | Date | 1 | 1～31
4 | 12803 | 3203 |  | Hour | 0 | 0～23
5 | 12804 | 3204 |  | Minute | 0 | 0～59
6 | 12805 | 3205 |  | Second | 0 | 0～59
7 | 12806 | 3206 |  | Millisecond | 0 | 0～999
Remark： 1.Set time with function code 0x10 (write). Read time of the meter with function code 03/04 (read). In order to prevent the occurrence of February 31st, the"Time" must be set with the command 10H. Otherwise it will be invalid. The clock chip will automatically turn milliseconds to zero. So milliseconds can be read-only.

## Zone 4XXX
Real-time Energy Zone - Four Quadrant LCD screen（Function Code 03/04 Read）
No. | Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
1 | 16384 | 4000 | Total Real-time Energy | Import Active Energy | 0 | 0～99999999.9
2 | 16385 | 4001
3 | 16386 | 4002 |  | Export Active Energy | 0 | 0～99999999.9
4 | 16387 | 4003
5 | 16388 | 4004 |  | Import Reactive Energy | 0 | 0～99999999.9
6 | 16389 | 4005
7 | 16390 | 4006 |  | Export Reactive Energy | 0 | 0～99999999.9
8 | 16391 | 4007
9 | 16392 | 4008 |  | Total Active Energy | 0 | 0～99999999.9
10 | 16393 | 4009
11 | 16394 | 400A |  | Total Reactive Energy | 0 | 0～99999999.9
12 | 16395 | 400B
13 | 16396 | 400C |  | Net Active Energy | 0 | 0～99999999.9
14 | 16397 | 400D
15 | 16398 | 400E |  | Net Reactive Energy | 0 | 0～99999999.9
16 | 16399 | 400F
17 | 16400 | 4010 |  | Apparent Energy | 0 | 0～99999999.9
18 | 16401 | 4011
19 | 16402 | 4012 |  | 1-quadrant Reactive Energy | 0 | 0～99999999.9
20 | 16403 | 4013
21 | 16404 | 4014 |  | 2-quadrant Reactive Energy | 0 | 0～99999999.9
22 | 16405 | 4015
23 | 16406 | 4016 |  | 3-quadrant Reactive Energy | 0 | 0～99999999.9
24 | 16407 | 4017
25 | 16408 | 4018 |  | 4-quadrant Reactive Energy | 0 | 0～99999999.9
26 | 16409 | 4019
27 | 16410 | 401A | Multi-tariff Real-time Energy | Sharp-period Import Active Energy | 0 | 0～99999999.9
28 | 16411 | 401B
29 | 16412 | 401C |  | Sharp-period Export Active Energy | 0 | 0～99999999.9
30 | 16413 | 401D
31 | 16414 | 401E |  | Sharp-period Import Reactive Energy | 0 | 0～99999999.9
32 | 16415 | 401F
33 | 16416 | 4020 |  | Sharp-period Export Reactive Energy | 0 | 0～99999999.9
34 | 16417 | 4021
35 | 16418 | 4022 |  | Sharp-period Total Active Energy | 0 | 0～99999999.9
36 | 16419 | 4023
37 | 16420 | 4024 |  | Sharp-period Total Reactive Energy | 0 | 0～99999999.9
38 | 16421 | 4025
39 | 16422 | 4026 |  | Sharp-period Net Active Energy | 0 | 0～99999999.9
40 | 16423 | 4027
41 | 16424 | 4028 |  | Sharp-period Net Reactive Energy | 0 | 0～99999999.9
42 | 16425 | 4029
43 | 16426 | 402A |  | Sharp-period Apparent Energy | 0 | 0～99999999.9
44 | 16427 | 402B
45 | 16428 | 402C |  | Sharp-period 1-quadrant Reactive Energy | 0 | 0～99999999.9
46 | 16429 | 402D
47 | 16430 | 402E |  | Sharp-period 2-quadrant Reactive Energy | 0 | 0～99999999.9
48 | 16431 | 402F
49 | 16432 | 4030 |  | Sharp-period 3-quadrant Reactive Energy | 0 | 0～99999999.9
50 | 16433 | 4031
51 | 16434 | 4032 |  | Sharp-period 4-quadrant Reactive Energy | 0 | 0～99999999.9
52 | 16435 | 4033
53 | 16436 | 4034 |  | Peak-period Energy (Remark 1) | 0 | 0～99999999.9
78 | 16461 | 404D
79 | 16462 | 404E |  | Off-peak-period Energy (Remark 1) | 0 | 0～99999999.9
104 | 16487 | 4067
105 | 16488 | 4068 |  | Shoulder-period Energy (Remark 1) | 0 | 0～99999999.9
130 | 16513 | 4081
Remark: 1.The registers for peak-period, off-peak period and shoulder-period energies refer to those for sharp-period energy. 2. Total real-time energy supports function code 04. Multi-tariff real-time energy doesn't support function code 04 but function code 03.
Multi-tariff Historical Energy Zone - Function Code 03 Read
| Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
1 | 16640 | 4100 | Present-month Energy | Total Energy | 0 | 0～99999999.9
26 | 16665 | 4119
27 | 16666 | 411A |  | Sharp-period Energy | 0 | 0～99999999.9
52 | 16691 | 4133
53 | 16692 | 4134 |  | Peak-period Energy | 0 | 0～99999999.9
78 | 16717 | 414D
79 | 16718 | 414E |  | Off-peak-period Energy | 0 | 0～99999999.9
104 | 16743 | 4167
105 | 16744 | 4168 |  | Shoulder-period Energy | 0 | 0～99999999.9
130 | 16769 | 4181
1 | 16896 | 4200 | Last 1st-Period Energy | Total Energy | 0 | 0～99999999.9
26 | 16921 | 4219
27 | 16922 | 421A |  | Sharp-period Energy | 0 | 0～99999999.9
52 | 16947 | 4233
53 | 16948 | 4234 |  | Peak-period Energy | 0 | 0～99999999.9
78 | 16973 | 424D
79 | 16974 | 424E |  | Off-peak-period Energy | 0 | 0～99999999.9
104 | 16999 | 4267
105 | 17000 | 4268 |  | Shoulder-period Energy | 0 | 0～99999999.9
130 | 17025 | 4281
1 | 17152 | 4300 | Last 2nd-Period Energy | Total Energy | 0 | 0～99999999.9
26 | 17177 | 4319
27 | 17178 | 431A |  | Sharp-period Energy | 0 | 0～99999999.9
52 | 17203 | 4333
53 | 17204 | 4334 |  | Peak-period Energy | 0 | 0～99999999.9
78 | 17229 | 434D
79 | 17230 | 434E |  | Off-peak-period Energy | 0 | 0～99999999.9
104 | 17255 | 4367
105 | 17256 | 4368 |  | Shoulder-period Energy | 0 | 0～99999999.9
130 | 17281 | 4381
1 | 17408 | 4400 | Last 3rd-Period Energy | Total Energy | 0 | 0～99999999.9
26 | 17433 | 4419
27 | 17434 | 441A |  | Sharp-period Energy | 0 | 0～99999999.9
52 | 17459 | 4433
53 | 17460 | 4434 |  | Peak-period Energy | 0 | 0～99999999.9
78 | 17485 | 444D
79 | 17486 | 444E |  | Off-peak-period Energy | 0 | 0～99999999.9
104 | 17511 | 4467
105 | 17512 | 4468 |  | Shoulder-period Energy | 0 | 0～99999999.9
130 | 17537 | 4481
1 | 17664 | 4500 | Last 4th-Period Energy | Total Energy | 0 | 0～99999999.9
26 | 17689 | 4519
27 | 17690 | 451A |  | Sharp-period Energy | 0 | 0～99999999.9
52 | 17715 | 4533
53 | 17716 | 4534 |  | Peak-period Energy | 0 | 0～99999999.9
78 | 17741 | 454D
79 | 17742 | 454E |  | Off-peak-period Energy | 0 | 0～99999999.9
104 | 17767 | 4567
105 | 17768 | 4568 |  | Shoulder-period Energy | 0 | 0～99999999.9
130 | 17793 | 4581
1 | 17920 | 4600 | Last 5th-Period Energy | Total Energy | 0 | 0～99999999.9
26 | 17945 | 4619
27 | 17946 | 461A |  | Sharp-period Energy | 0 | 0～99999999.9
52 | 17971 | 4633
53 | 17972 | 4634 |  | Peak-period Energy | 0 | 0～99999999.9
78 | 17997 | 464D
79 | 17998 | 464E |  | Off-peak-period Energy | 0 | 0～99999999.9
104 | 18023 | 4667
105 | 18024 | 4668 |  | Shoulder-period Energy | 0 | 0～99999999.9
130 | 18049 | 4681
1 | 18176 | 4700 | Last 6th-Period Energy | Total Energy | 0 | 0～99999999.9
26 | 18201 | 4719
27 | 18202 | 471A |  | Sharp-period Energy | 0 | 0～99999999.9
52 | 18227 | 4733
53 | 18228 | 4734 |  | Peak-period Energy | 0 | 0～99999999.9
78 | 18253 | 474D
79 | 18254 | 474E |  | Off-peak-period Energy | 0 | 0～99999999.9
104 | 18279 | 4767
105 | 18280 | 4768 |  | Shoulder-period Energy | 0 | 0～99999999.9
130 | 18305 | 4781
1 | 18432 | 4800 | Last 7th-Period Energy | Total Energy | 0 | 0～99999999.9
26 | 18457 | 4819
27 | 18458 | 481A |  | Sharp-period Energy | 0 | 0～99999999.9
52 | 18483 | 4833
53 | 18484 | 4834 |  | Peak-period Energy | 0 | 0～99999999.9
78 | 18509 | 484D
79 | 18510 | 484E |  | Off-peak-period Energy | 0 | 0～99999999.9
104 | 18535 | 4867
105 | 18536 | 4868 |  | Shoulder-period Energy | 0 | 0～99999999.9
130 | 18561 | 4881
1 | 18688 | 4900 | Last 8th-Period Energy | Total Energy | 0 | 0～99999999.9
26 | 18713 | 4919
27 | 18714 | 491A |  | Sharp-period Energy | 0 | 0～99999999.9
52 | 18739 | 4933
53 | 18740 | 4934 |  | Peak-period Energy | 0 | 0～99999999.9
78 | 18765 | 494D
79 | 18766 | 494E |  | Off-peak-period Energy | 0 | 0～99999999.9
104 | 18791 | 4967
105 | 18792 | 4968 |  | Shoulder-period Energy | 0 | 0～99999999.9
130 | 18817 | 4981
1 | 18944 | 4A00 | Last 9th-Period Energy | Total Energy | 0 | 0～99999999.9
26 | 18969 | 4A19
27 | 18970 | 4A1A |  | Sharp-period Energy | 0 | 0～99999999.9
52 | 18995 | 4A33
53 | 18996 | 4A34 |  | Peak-period Energy | 0 | 0～99999999.9
78 | 19021 | 4A4D
79 | 19022 | 4A4E |  | Off-peak-period Energy | 0 | 0～99999999.9
104 | 19047 | 4A67
105 | 19048 | 4A68 |  | Shoulder-period Energy | 0 | 0～99999999.9
130 | 19073 | 4A81
1 | 19200 | 4B00 | Last 10th-Period Energy | Total Energy | 0 | 0～99999999.9
26 | 19225 | 4B19
27 | 19226 | 4B1A |  | Sharp-period Energy | 0 | 0～99999999.9
52 | 19251 | 4B33
53 | 19252 | 4B34 |  | Peak-period Energy | 0 | 0～99999999.9
78 | 19277 | 4B4D
79 | 19278 | 4B4E |  | Off-peak-period Energy | 0 | 0～99999999.9
104 | 19303 | 4B67
105 | 19304 | 4B68 |  | Shoulder-period Energy | 0 | 0～99999999.9
130 | 19329 | 4B81
1 | 19456 | 4C00 | Last 11th-Period Energy | Total Energy | 0 | 0～99999999.9
26 | 19481 | 4C19
27 | 19482 | 4C1A |  | Sharp-period Energy | 0 | 0～99999999.9
52 | 19507 | 4C33
53 | 19508 | 4C34 |  | Peak-period Energy | 0 | 0～99999999.9
78 | 19533 | 4C4D
79 | 19534 | 4C4E |  | Off-peak-period Energy | 0 | 0～99999999.9
104 | 19559 | 4C67
105 | 19560 | 4C68 |  | Shoulder-period Energy | 0 | 0～99999999.9
130 | 19585 | 4C81
Remark: 1. Total real-time energy for sharp-period, peak-period, off-peak period and shoulder-period energies refer to those in real-time energy zone.

## Formulas
Formulas Between Real Values and Modbus Registers' Values(Rx：Modbus Registers' Values)
Parameters | Formula | Unit
Voltage: Ua,Ub,Uc,Uab,Ubc,Uca,Un | U＝Rx×PT/100 | V
Current: Ia,Ib,Ic，In | I＝Rx×CT/1000 | A
Active Power: Pa, Pb, Pc, Psum | P＝Rx×PT×CT | W
Reactive Power: Qa, Qb，Qc，Qsum | Q＝Rx×PT×CT | Var
Apparent Power: Ssum | S＝Rx×PT×CT | VA
Power Factor: PFa，PFb，PFc，Pfsum | PF＝Rx/100
Frequency: F | F＝Rx/100 | Hz
Load Property Rt(resistive / inductive / capacitive) | 0/1/2/
Unbalance Factor : U_unbl,I_unbl | Unbl=(Rx/10000)×100％
Harmonic Content | Unbl=(Rx/1000)×100％ | ％