## Zone 1XXX
Basic Parameters Measured Zone（Function Code 03/04 Read）
| Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
1 | 4096 | 1000 | Phase Voltage | phase A voltage | magnifying 100 times | 0～65535
2 | 4097 | 1001 |  | phase B voltage | magnifying 100 times | 0～65535
3 | 4098 | 1002 |  | phase C voltage | magnifying 100 times | 0～65535
4 | 4099 | 1003 |  | phase voltage mean value | magnifying 100 times | 0～65535
5 | 4100 | 1004 |  | zero sequence voltage | magnifying 100 times | 0～65535
6 | 4101 | 1005 | Line Voltage | line voltage(A-B) | magnifying 100 times | 0～65535
7 | 4102 | 1006 |  | line voltage(B-C) | magnifying 100 times | 0～65535
8 | 4103 | 1007 |  | line voltage(C-A) | magnifying 100 times | 0～65535
9 | 4104 | 1008 |  | line voltage mean value | magnifying 100 times | 0～65535
10 | 4105 | 1009 | Current | phase/line Current of phase A | magnifying 1,000 times | 0～65535
11 | 4106 | 100A |  | phase/line Current of phase B | magnifying 1,000 times | 0～65535
12 | 4107 | 100B |  | phase/line Current of phase C | magnifying 1,000 times | 0～65535
13 | 4108 | 100C |  | phase/line Current mean value | magnifying 1,000 times | 0～65535
14 | 4109 | 100D |  | zero sequence current | magnifying 1,000 times | 0～65535
15 | 4110 | 100E | Active Power | active power of phase A | magnifying 1,000 times | -32768～32767
16 | 4111 | 100F |  | active power of phase B | magnifying 1,000 times | -32768～32767
17 | 4112 | 1010 |  | active power of phase C | magnifying 1,000 times | -32768～32767
18 | 4113 | 1011 |  | total three-phase active power | magnifying 1,000 times | -32768～32767
19 | 4114 | 1012 | Reactive Power | reactive power of phase A | magnifying 1,000 times | -32768～32767
20 | 4115 | 1013 |  | reactive power of phase B | magnifying 1,000 times | -32768～32767
21 | 4116 | 1014 |  | reactive power of phase C | magnifying 1,000 times | -32768～32767
22 | 4117 | 1015 |  | total three-phase reactive power | magnifying 1,000 times | -32768～32767
23 | 4118 | 1016 | Apparent Power | apparent power of phase A | magnifying 1,000 times | -32768～32767
24 | 4119 | 1017 |  | apparent power of phase B | magnifying 1,000 times | -32768～32767
25 | 4120 | 1018 |  | apparent power of phase C | magnifying 1,000 times | -32768～32767
26 | 4121 | 1019 |  | total three-phase apparent power | magnifying 1,000 times | -32768～32767
27 | 4122 | 101A | Power Factor | power factor of phase A | magnifying 100 times | -100～100
28 | 4123 | 101B |  | power factor of phase B | magnifying 100 times | -100～100
29 | 4124 | 101C |  | power factor of phase C | magnifying 100 times | -100～100
30 | 4125 | 101D |  | total three-phase power factor | magnifying 100 times | -100～100
31 | 4126 | 101E | Frequency | frequency | magnifying 100 times | 0～65535
32 | 4127 | 101F | Unbalance Factor | voltage unbalance factor | magnifying 10,000 times | 0～100
33 | 4128 | 1020 |  | current unbalance factor | magnifying 10,000 times | 0～100

## Zone 2XXX
Basic Parameters Measured Zone（Function Code 06/0x10 Write; Function Code 03/04 Read）
No. | Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
1 | 8192 | 2000 | Basic Parameters | password protection (protection of basic parameters) | 0 | 0～9999
2 | 8193 | 2001 |  | meter communication address | 1 | 1～247
3 | 8194 | 2002 |  | RS485 serial port parameter （high byte is parity check; low byte is baud rate） | 3 | High：0:(N,8,1)，1:(E,8,1)，2:(O,8,1) Low：0:9600, 1:2400, 2:4800, 3:9600，4:19200
4 | 8195 | 2003 |  | voltage wiring mode | 0 | 0：3LN，1：2LN，2：2LL
5 | 8196 | 2004 |  | current wiring mode | 0 | 0：3CT，1：2CT，2：1CT
6 | 8197 | 2005 |  | PT | 1 | 1∼9999 Remark 1
7 | 8198 | 2006 |  | CT | 1 | 1～9999 Remark 1
8 | 8199 | 2007 |  | shift between primary energy and secondary energy | 0 | 0：secondary Energy，1：primary Energy
11 | 8202 | 200A |  | Selection of Pulse Energy Output Through DO1 Port | 1 | 0: Overcurrent alarm pulse 1：Import Active Energy, 2：Export Active Energy 3：Import Reactive Energy，4：Export Reactive Energy 5：Absolute Value & Active Energy，6：Absolute Value & Reactive Energy 7：Net Active Energy，8：Net Reactive Energy 9：Apparent Energy
12 | 8203 | 200B |  | Selection of Pulse Energy Output Through DO2 Port | 2 | 0: Trend of Current/ Vlotage Record 1：Import Active Energy, 2：Export Active Energy 3：Import Reactive Energy，4：Export Reactive Energy 5：Absolute Value & Active Energy，6：Absolute Value & Reactive Energy 7：Net Active Energy，8：Net Reactive Energy 9：Apparent Energy
13 | 8204 | 200C |  | energy decimal places | 1 | 0～4
14 | 8205 | 200D |  | spare | -- | 0
15 | 8206 | 200E |  | energy pulse constant | 9600 | 600～50000
16 | 8207 | 200F |  | backlight time | 100 | 0～999
17 | 8208 | 2010 | DO | DO1 Setting | 0x40c8 | bit15:function selection 0：Tele-control，1：Alarm； bit14:Working Mode Selection 0：Electrical Level，1：pulse； bit0～bit13: Pulse Width，range：50～3000ms remark 2
18 | 8209 | 2011 |  | DO2 Setting | 0x40c8
19 | 8210 | 2012 |  | DO3 Setting | 0x40c8
20 | 8211 | 2013 |  | DO4 Setting | 0x40c8
21 | 8212 | 2014 |  | spare | -- | 0
22 | 8213 | 2015 |  | spare | -- | 0
23 | 8214 | 2016 |  | spare | -- | 0
24 | 8215 | 2017 |  | spare | -- | 0
25 | 8216 | 2018 | Alarm | enable alarm function | 0 | 0：Close Alarm 1：Open Alarm
| 8217 | 2019 |  | enable alarm setting | 0 | ( 0：Reactive 1：Active ) remark 3 range（0～0xFFFF）
| 8218 | 201A |  | enable alarm flash | 0 | LCD Backlight: 0：Unflashing 1：Flashing
| 8219 | 201B |  | alarm output through DO1 | 0 | (0：Reactive 1：Active ) Remark 4 range（0～0xFFFF）
| 8220 | 201C |  | alarm output through DO2 | 0 | (0：Reactive 1：Active ) Remark 4 range（0～0xFFFF）
Remark： 1.The product of CT and PT should be less than 300,000. 2. If the purpose of the relay is set as alarm, the settings of pulse mode and pulse width will be invalid and can only be used as the level mode output. If the relay is set as the level mode, the pulse width will be invalid. 3. E.g. if the register is 0x0101（00000001 00000001B）, i.e., the alarm parameter setting of the 1st and the 9th groups can trigger the alarm function. 4. E.g. if the register of 0x201B was set as 0x01010x0101（00000001 00000001B）, i.e., the alarm parameter setting of the 1st or the 9th groups can trigger the alarm function. Besides, if the register（0x2010）use of DO1 is set as 1(alarm output),the DO1 will be connected. When the alarm recovers, the relay will be disconnected. 5. E.g. if under the DI wave recording mode, the register1（0x201D）is set as 0x0011（0001 0001B),i.e.if the status of DI1&DI3 is connected,it will start recording wave. DI2&DI4 will not record wave.

## Zone 3XXX
Real-time Clock Zone（（Function Code 0x10 Write; Function Code 03/04 Read）
No. | Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
1 | 12800 | 3200 | Time | Year | 2000 | 2000～2099
2 | 12801 | 3201 |  | Month | 1 | 1～12
3 | 12802 | 3202 |  | Date | 1 | 1～31
4 | 12803 | 3203 |  | Hour | 0 | 0～23
5 | 12804 | 3204 |  | Minute | 0 | 0～59
6 | 12805 | 3205 |  | Second | 0 | 0～59
7 | 12806 | 3206 |  | Millisecond | 0 | 0～999
Remark： 1.Set time with function code 0x10 (write). Read time of the meter with function code 03/04 (read). In order to prevent the occurrence of February 31st, the"Time" must be set with the command 10H. Otherwise it will be invalid. The clock chip will automatically turn milliseconds to zero. So milliseconds can be read-only.

## Zone 4XXX
Real-time Energy Zone - Four Quadrant LCD screen（Function Code 03/04 Read）
No. | Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
1 | 16384 | 4000 | Total Real-time Energy | Import Active Energy | 0 | 0～99999999.9
2 | 16385 | 4001
3 | 16386 | 4002 |  | Export Active Energy | 0 | 0～99999999.9
4 | 16387 | 4003
5 | 16388 | 4004 |  | Import Reactive Energy | 0 | 0～99999999.9
6 | 16389 | 4005
7 | 16390 | 4006 |  | Export Reactive Energy | 0 | 0～99999999.9
8 | 16391 | 4007
9 | 16392 | 4008 |  | Total Active Energy | 0 | 0～99999999.9
10 | 16393 | 4009
11 | 16394 | 400A |  | Total Reactive Energy | 0 | 0～99999999.9
12 | 16395 | 400B
13 | 16396 | 400C |  | Net Active Energy | 0 | 0～99999999.9
14 | 16397 | 400D
15 | 16398 | 400E |  | Net Reactive Energy | 0 | 0～99999999.9
16 | 16399 | 400F
17 | 16400 | 4010 |  | Apparent Energy | 0 | 0～99999999.9
18 | 16401 | 4011
19 | 16402 | 4012 |  | 1-quadrant Reactive Energy | 0 | 0～99999999.9
20 | 16403 | 4013
21 | 16404 | 4014 |  | 2-quadrant Reactive Energy | 0 | 0～99999999.9
22 | 16405 | 4015
23 | 16406 | 4016 |  | 3-quadrant Reactive Energy | 0 | 0～99999999.9
24 | 16407 | 4017
25 | 16408 | 4018 |  | 4-quadrant Reactive Energy | 0 | 0～99999999.9
26 | 16409 | 4019
Remark: 1.The registers for peak-period, off-peak period and shoulder-period energies refer to those for sharp-period energy. 2. Total real-time energy supports function code 04. Multi-tariff real-time energy doesn't support function code 04 but function code 03.

## Formulas
Formulas Between Real Values and Modbus Registers' Values(Rx：Modbus Registers' Values)
Parameters | Formula | Unit
Voltage: Ua,Ub,Uc,Uab,Ubc,Uca,Un | U＝Rx×PT/100 | V
Current: Ia,Ib,Ic，In | I＝Rx×CT/1000 | A
Active Power: Pa, Pb, Pc, Psum | P＝Rx×PT×CT | W
Reactive Power: Qa, Qb，Qc，Qsum | Q＝Rx×PT×CT | Var
Apparent Power: Ssum | S＝Rx×PT×CT | VA
Power Factor: PFa，PFb，PFc，Pfsum | PF＝Rx/100
Frequency: F | F＝Rx/100 | Hz
Load Property Rt(resistive / inductive / capacitive) | 0/1/2/
Unbalance Factor : U_unbl,I_unbl | Unbl=(Rx/10000)×100％
Harmonic Content | Unbl=(Rx/1000)×100％ | ％