## Sheet 1
Anolog Input(Function Code 03/04 Read)
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Format | Remark
10 | 0X000A | ALARM | alarm indication sign | WORD | （Remark A）
11 | 0X000B | protect | protection action and fault sign | WORD | （Remark B）
12 | 0X000C | 3V0 | three phase unbalanced voltage(3U0) | WORD
13 | 0X000D | BREAD_V | three phase voltage unbalance degree(%) | WORD | （Remark C）
14 | 0X000E | BREAD_I | three phase current unbalance degree(%) | WORD | （Remark C）
15 | 0X000F | I/O | digital input and output status | WORD | （Remark D）
16 | 0X0010 | IA | effective value of phase A current | WORD
17 | 0X0011 | IB | effective value of phase B current | WORD
18 | 0X0012 | IC | effective value of phase C current | WORD
19 | 0X0013 | 3I0 | three phase unbalanced current(3I0) | WORD
20 | 0X0014 | VAn | effective value of phase A voltage | WORD
21 | 0X0015 | VBn | effective value of phase B voltage | WORD
22 | 0X0016 | VCn | effective value of phase C voltage | WORD
23 | 0X0017 | VAB | effective value of line A-B voltage | WORD
24 | 0X0018 | VBC | effective value of line B-C voltage | WORD
25 | 0X0019 | VCA | effective value of line C-A voltage | WORD
26 | 0X001A | W | active power | WORD
27 | 0X001B | VAR | reactive power | WORD
28 | 0X001C | VA | apparent power | WORD
29 | 0X001D | PF | power factor | WORD
30 | 0X001E | FREQ | frequency | WORD
31 | 0X001F | WA | phase A active power | WORD
32 | 0X0020 | WB | phase B active power | WORD
33 | 0X0021 | WC | phase C active power | WORD
34 | 0X0022 | varA | phase A reactive power | WORD
35 | 0X0023 | varB | phase B reactive power | WORD
36 | 0X0024 | varC | phase C reactive power | WORD
37 | 0X0025 | vaA | phase A apparent power | WORD
38 | 0X0026 | vaB | phase B apparent powe | WORD
39 | 0X0027 | vaC | phase C apparent powe | WORD
40 | 0X0028 | PFA | phase A power factor | WORD
41 | 0X0029 | PFB | phase B power factor | WORD
42 | 0X002A | PFC | phase C power factor | WORD
43 | 0X002B | AVER_A | three phase current average value | WORD
44 | 0X002C | AVER_VN | phase voltage average value of three phases | WORD
45 | 0X002D | AVER_VX | line voltage average value of three phases | WORD
46 | 0X002E | kvarh | high byte of import total reactive energy | WORD
47 | 0X002F |  | low byte of import total reactive energy | WORD | （Remark E）
48 | 0X0030 | kWh | high byte of import total active energy | WORD
49 | 0X0031 |  | low byte of import total active energy | WORD
50 | 0X0032 | kvarh -J | high byte of import total reactive energy in sharp period | WORD
51 | 0X0033 |  | low byte of import total reactive energy in sharp period | WORD
52 | 0X0034 | kWh -J | high byte of import total active energy in sharp period | WORD
53 | 0X0035 |  | low byte of import total active energy in sharp period | WORD
54 | 0X0036 | kvarh -F | high byte of import total reactive energy in peak period | WORD
55 | 0X0037 |  | low byte of import total reactive energy in peak period | WORD
56 | 0X0038 | kWh -F | high byte of import total active energy in peak period | WORD
57 | 0X0039 |  | low byte of import total active energy in peak period | WORD
58 | 0X003A | kvarh -P | high byte of import total reactive energy in shoulder period | WORD
59 | 0X003B |  | low byte of import total reactive energy in shoulder period | WORD
60 | 0X003C | kWh -P | high byte of import total active energy in shoulder period | WORD
61 | 0X003D |  | low byte of import total active energy in shoulder period | WORD
62 | 0X003E | kvarh -G | high byte of import total reactive energy in off-peak period | WORD
63 | 0X003F |  | low byte of import total reactive energy in off-peak period | WORD
64 | 0X0040 | kWh -G | high byte of import total active energy in off-peak period | WORD
65 | 0X0041 |  | high byte of import total active energy in off-peak period | WORD
66 | 0X0042 | Kvarh-NE | high byte of export total reactive energy | WORD
67 | 0X0043 |  | low byte of export total reactive energy | WORD
68 | 0X0044 | kWh-NE | high byte of export total active energy | WORD
69 | 0X0045 |  | low byte of export total active energy | WORD
70 | 0X0046 | kvarh -J-NE | high byte of export total reactive energy in sharp period | WORD
71 | 0X0047 |  | low byte of export total reactive energy in sharp period | WORD
72 | 0X0048 | kWh -J-NE | high byte of export total active energy in sharp period | WORD
73 | 0X0049 |  | low byte of export total active energy in sharp period | WORD
74 | 0X004A | kvarh -F-NE | high byte of export total reactive energy in peak period | WORD
75 | 0X004B |  | low byte of export total reactive energy in peak period | WORD
76 | 0X004C | kWh -F-NE | high byte of export total active energy in peak period | WORD
77 | 0X004D |  | low byte of export total active energy in peak period | WORD
78 | 0X004E | kvarh -P-NE | high byte of export total reactive energy in shoulder period | WORD
79 | 0X004F |  | low byte of export total reactive energy in shoulder period | WORD
80 | 0X0050 | kWh -P-NE | high byte of export total active energy in shoulder period | WORD
81 | 0X0051 |  | low byte of export total active energy in shoulder period | WORD
82 | 0X0052 | kvarh -G-NE | high byte of export total reactive energy in off-peak period | WORD
83 | 0X0053 |  | low byte of export total reactive energy in off-peak period | WORD
84 | 0X0054 | kWh -G-NE | high byte of export total active energy in off-peak period | WORD
85 | 0X0055 |  | high byte of export total active energy in off-peak period | WORD
96 | 0x0060 | IA-MAX | phase A maximum current within period | WORD
97 | 0x0061 | IB-MAX | phase B maximum current within period | WORD
98 | 0x0062 | IC-MAX | phase C maximum current within period | WORD
99 | 0x0063 | W-MAX | maximum total active power within period | WORD
100 | 0x0064 | VAR-MAX | maximum total reactive power within period | WORD
101 | 0x0065 | PF-MAX | maximum power factor within period | WORD
102 | 0x0066 | IA-MIN | phase A minimum current within period | WORD
103 | 0x0067 | IB-MIN | phase B minimum current within period | WORD
104 | 0x0068 | IC-MIN | phase C minimum current within period | WORD
105 | 0x0069 | W-MIN | minimum total active power within period | WORD
106 | 0x006A | VAR-MIN | minimum total reactive power within period | WORD
107 | 0x006B | PF-MIN | minimum power factor within period | WORD
108 | 0x006C | IA-AVR | phase A current average value within period | WORD
109 | 0x006D | IB- AVR | phase B current average value within period | WORD
110 | 0x006E | IC- AVR | phase C current average value within period | WORD
111 | 0x006F | W- AVR | total active power average value within period | WORD
112 | 0x0070 | VAR- AVR | total reactive power average value within period | WORD
113 | 0x0071 | PF- AVR | total power factor average value within period | WORD
Remark A：Alarm Indicator Flag Bit
No. | Address | Flag Bit | Fault Signal | Active Virtual Value | Format | Instruction
1 | 0X000A | Bit0 | Over Current | 1 | Bit
2 | 0X000A | Bit1 | Over Voltage | 1 | Bit
3 | 0X000A | Bit2 | under voltage | 1 | Bit
4 | 0X000A | Bit3 | Phase Loss | 1 | Bit
5 | 0X000A | Bit4 | Unblance | 1 | Bit
6 | 0X000A | Bit5 | Blank | 1 | Bit
7 | 0X000A | Bit6 | Blank | 1 | Bit
8 | 0X000A | Bit7 | Total Alarm | 1 | Bit
9 | 0X000A | Bit8 | Blank | 1 | Bit
10 | 0X000A | Bit9 | Blank | 1 | Bit
11 | 0X000A | Bit10 | Blank | 1 | Bit
12 | 0X000A | Bit11 | Blank | 1 | Bit
13 | 0X000A | Bit12 | Blank | 1 | Bit
14 | 0X000A | Bit13 | Blank | 1 | Bit
15 | 0X000A | Bit14 | Blank | 1 | Bit
16 | 0X000A | Bit15 | Total Alarm | 1 | Bit
Remark：B Protection and Fault Indicator
No. | Address | Flag Bit | Fault Signal | Active Virtual Value | Format | Instruction
1 | 0X000B | Bit0 | Over Current | 1 | Bit
2 | 0X000B | Bit1 | Over Voltage | 1 | Bit
3 | 0X000B | Bit2 | under voltage | 1 | Bit
4 | 0X000B | Bit3 | Phase Loss | 1 | Bit
5 | 0X000B | Bit4 | Unblance | 1 | Bit
6 | 0X000B | Bit5 | Blank | 1 | Bit
7 | 0X000B | Bit6 | Blank | 1 | Bit
8 | 0X000B | Bit7 | DI1 | 1 | Bit
9 | 0X000B | Bit8 | DI2 | 1 | Bit
10 | 0X000B | Bit9 | DI3 | 1 | Bit
11 | 0X000B | Bit10 | DI4 | 1 | Bit
12 | 0X000B | Bit11 | Clear Energy | 1 | Bit
13 | 0X000B | Bit12 | Blank | 1 | Bit
14 | 0X000B | Bit13 | Blank | 1 | Bit
15 | 0X000B | Bit14 | Blank | 1 | Bit
16 | 0X000B | Bit15 | Trip Indication | 1 | Bit
Remark C：The value of the unblance degree is expressed as a percentage. (the maximum value -the minimum value)/ the maximum value
Remark D：I/O Digital Input&output Statue
No. | Address | Flag Bit | Statue Signal | Active Virtual Value | Format | Instruction
1 | X000F | Bit0 | DI1 | 1 | Bit
2 | X000F | Bit1 | DI2 | 1 | Bit
3 | X000F | Bit2 | Blank | 1 | Bit
4 | X000F | Bit3 | Blank | 1 | Bit
5 | X000F | Bit4 | Blank | 1 | Bit
6 | X000F | Bit5 | Blank | 1 | Bit
7 | X000F | Bit6 | Blank | 1 | Bit
8 | X000F | Bit7 | Blank | 1 | Bit
9 | X000F | Bit8 | Q1 | 1 | Bit
10 | X000F | Bit9 | Q2 | 1 | Bit
11 | X000F | Bit10 | Blank | 1 | Bit
12 | X000F | Bit11 | Blank | 1 | Bit
13 | X000F | Bit12 | Blank | 1 | Bit
14 | X000F | Bit13 | Blank | 1 | Bit
15 | X000F | Bit14 | Blank | 1 | Bit
16 | X000F | Bit15 | Blank | 1 | Bit
Digital Input（Function Code “02”）statue address is start from 0000 Eg.：Read the data of address 0X000F is 0X0201, that means the output Q2 is connection, input DI1 is connection, others are disconnection
*Remark E：Energy value is stored in 4-byte hexadecimal unsigned double-word mode, the high byte is in front, the lower byte is after and with 1 decimal place. KVARH-hex、Kwh-hex energy value = corresponding energy value high byte×0x10000 +corresponding energy value lower byte, i.g. the actual reading energy value high byte * 65536, then plus the lower byte-—HEX mode eg：the register 0X0030start 4 bytes data is：03 45 78 12，so the energy value is : 0x03457812 = 5488437.0 kwh The measuring energy value range is 0-99999999.9.
*Remark F:Relay Output Flag Bit （Fucntion Code 05）
No. | Address | Instruction | Flag Bit | Command
1 | 0X0000 | Relay 1 | Bit0 | Connection：FF00
Disconnection：0000
2 | 0X0001 | Relay 2 | Bit1 | Connection：FF00
Disconnection：0000

## Sheet 2
THD（03/04 Function Code）
| Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Format | Remark
| 1 | 0X0001 | total harmonic distortion rate (THD) | THD Ua | WORD
| 2 | 0X0002 |  | THD Ub | WORD
| 3 | 0X0003 |  | THD Uc | WORD
| 4 | 0X0004 |  | THD Ia | WORD
| 5 | 0X0005 |  | THD Ib | WORD
| 6 | 0X0006 |  | THD Ic | WORD
0-31st harmonic content（03/04 Function Code）
| Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Format | Remark
0 | 1904 | 0X0770 | Voltage Ua harmonic content | 0 harmonic content | WORD
1 | 1905 | 0X0771 |  | 1st harmonic content | WORD
2 | 1906 | 0X0772 |  | 2nd harmonic content | WORD
3 | 1907 | 0X0773 |  | 3rd harmonic content | WORD
4 | 1908 | 0X0774 |  | 4th harmonic content | WORD
5 | 1909 | 0X0775 |  | 5th harmonic content | WORD
6 | 1910 | 0X0776 |  | 6th harmonic content | WORD
7 | 1911 | 0X0777 |  | 7th harmonic content | WORD
8 | 1912 | 0X0778 |  | 8th harmonic content | WORD
9 | 1913 | 0X0779 |  | 9th harmonic content | WORD
10 | 1914 | 0X077A |  | 10th harmonic content | WORD
11 | 1915 | 0X077B |  | 11st harmonic content | WORD
12 | 1916 | 0X077C |  | 12nd harmonic content | WORD
13 | 1917 | 0X077D |  | 13rd harmonic content | WORD
14 | 1918 | 0X077E |  | 14th harmonic content | WORD
15 | 1919 | 0X077F |  | 15th harmonic content | WORD
16 | 1920 | 0X0780 |  | 16th harmonic content | WORD
17 | 1921 | 0X0781 |  | 17th harmonic content | WORD
18 | 1922 | 0X0782 |  | 18th harmonic content | WORD
19 | 1923 | 0X0783 |  | 19th harmonic content | WORD
20 | 1924 | 0X0784 |  | 20th harmonic content | WORD
21 | 1925 | 0X0785 |  | 21st harmonic content | WORD
22 | 1926 | 0X0786 |  | 22nd harmonic content | WORD
23 | 1927 | 0X0787 |  | 23rd harmonic content | WORD
24 | 1928 | 0X0788 |  | 24th harmonic content | WORD
25 | 1929 | 0X0789 |  | 25th harmonic content | WORD
26 | 1930 | 0X078A |  | 26th harmonic content | WORD
27 | 1931 | 0X078B |  | 27th harmonic content | WORD
28 | 1932 | 0X078C |  | 28th harmonic content | WORD
29 | 1933 | 0X078D |  | 29th harmonic content | WORD
30 | 1934 | 0X078E |  | 30th harmonic content | WORD
31 | 1935 | 0X078F |  | 31st harmonic content | WORD
| 1936 | 0X0790 | Voltage Ub harmonic content | 0 harmonic content | WORD
| 1937 | 0X0791 |  | 1st harmonic content | WORD
| 1938 | 0X0792 |  | 2nd harmonic content | WORD
| 1939 | 0X0793 |  | 3rd harmonic content | WORD
| 1940 | 0X0794 |  | 4th harmonic content | WORD
| 1941 | 0X0795 |  | 5th harmonic content | WORD
| 1942 | 0X0796 |  | 6th harmonic content | WORD
| 1943 | 0X0797 |  | 7th harmonic content | WORD
| 1944 | 0X0798 |  | 8th harmonic content | WORD
| 1945 | 0X0799 |  | 9th harmonic content | WORD
| 1946 | 0X079A |  | 10th harmonic content | WORD
| 1947 | 0X079B |  | 11st harmonic content | WORD
| 1948 | 0X079C |  | 12nd harmonic content | WORD
| 1949 | 0X079D |  | 13rd harmonic content | WORD
| 1950 | 0X079E |  | 14th harmonic content | WORD
| 1951 | 0X079F |  | 15th harmonic content | WORD
| 1952 | 0X07A0 |  | 16th harmonic content | WORD
| 1953 | 0X07A1 |  | 17th harmonic content | WORD
| 1954 | 0X07A2 |  | 18th harmonic content | WORD
| 1955 | 0X07A3 |  | 19th harmonic content | WORD
| 1956 | 0X07A4 |  | 20th harmonic content | WORD
| 1957 | 0X07A5 |  | 21st harmonic content | WORD
| 1958 | 0X07A6 |  | 22nd harmonic content | WORD
| 1959 | 0X07A7 |  | 23rd harmonic content | WORD
| 1960 | 0X07A8 |  | 24th harmonic content | WORD
| 1961 | 0X07A9 |  | 25th harmonic content | WORD
| 1962 | 0X07AA |  | 26th harmonic content | WORD
| 1963 | 0X07AB |  | 27th harmonic content | WORD
| 1964 | 0X07AC |  | 28th harmonic content | WORD
| 1965 | 0X07AD |  | 29th harmonic content | WORD
| 1966 | 0X07AE |  | 30th harmonic content | WORD
| 1967 | 0X07AF |  | 31st harmonic content | WORD
| 1968 | 0X07B0 | Voltage Uc harmonic content | 0 harmonic content | WORD
| 1969 | 0X07B1 |  | 1st harmonic content | WORD
| 1970 | 0X07B2 |  | 2nd harmonic content | WORD
| 1971 | 0X07B3 |  | 3rd harmonic content | WORD
| 1972 | 0X07B4 |  | 4th harmonic content | WORD
| 1973 | 0X07B5 |  | 5th harmonic content | WORD
| 1974 | 0X07B6 |  | 6th harmonic content | WORD
| 1975 | 0X07B7 |  | 7th harmonic content | WORD
| 1976 | 0X07B8 |  | 8th harmonic content | WORD
| 1977 | 0X07B9 |  | 9th harmonic content | WORD
| 1978 | 0X07BA |  | 10th harmonic content | WORD
| 1979 | 0X07BB |  | 11st harmonic content | WORD
| 1980 | 0X07BC |  | 12nd harmonic content | WORD
| 1981 | 0X07BD |  | 13rd harmonic content | WORD
| 1982 | 0X07BE |  | 14th harmonic content | WORD
| 1983 | 0X07BF |  | 15th harmonic content | WORD
| 1984 | 0X07C0 |  | 16th harmonic content | WORD
| 1985 | 0X07C1 |  | 17th harmonic content | WORD
| 1986 | 0X07C2 |  | 18th harmonic content | WORD
| 1987 | 0X07C3 |  | 19th harmonic content | WORD
| 1988 | 0X07C4 |  | 20th harmonic content | WORD
| 1989 | 0X07C5 |  | 21st harmonic content | WORD
| 1990 | 0X07C6 |  | 22nd harmonic content | WORD
| 1991 | 0X07C7 |  | 23rd harmonic content | WORD
| 1992 | 0X07C8 |  | 24th harmonic content | WORD
| 1993 | 0X07C9 |  | 25th harmonic content | WORD
| 1994 | 0X07CA |  | 26th harmonic content | WORD
| 1995 | 0X07CB |  | 27th harmonic content | WORD
| 1996 | 0X07CC |  | 28th harmonic content | WORD
| 1997 | 0X07CD |  | 29th harmonic content | WORD
| 1998 | 0X07CE |  | 30th harmonic content | WORD
| 1999 | 0X07CF |  | 31st harmonic content | WORD
| 2000 | 0X07D0 | Voltage Ia harmonic content | 0 harmonic content | WORD
| 2001 | 0X07D1 |  | 1st harmonic content | WORD
| 2002 | 0X07D2 |  | 2nd harmonic content | WORD
| 2003 | 0X07D3 |  | 3rd harmonic content | WORD
| 2004 | 0X07D4 |  | 4th harmonic content | WORD
| 2005 | 0X07D5 |  | 5th harmonic content | WORD
| 2006 | 0X07D6 |  | 6th harmonic content | WORD
| 2007 | 0X07D7 |  | 7th harmonic content | WORD
| 2008 | 0X07D8 |  | 8th harmonic content | WORD
| 2009 | 0X07D9 |  | 9th harmonic content | WORD
| 2010 | 0X07DA |  | 10th harmonic content | WORD
| 2011 | 0X07DB |  | 11st harmonic content | WORD
| 2012 | 0X07DC |  | 12nd harmonic content | WORD
| 2013 | 0X07DD |  | 13rd harmonic content | WORD
| 2014 | 0X07DE |  | 14th harmonic content | WORD
| 2015 | 0X07DF |  | 15th harmonic content | WORD
| 2016 | 0X07E0 |  | 16th harmonic content | WORD
| 2017 | 0X07E1 |  | 17th harmonic content | WORD
| 2018 | 0X07E2 |  | 18th harmonic content | WORD
| 2019 | 0X07E3 |  | 19th harmonic content | WORD
| 2020 | 0X07E4 |  | 20th harmonic content | WORD
| 2021 | 0X07E5 |  | 21st harmonic content | WORD
| 2022 | 0X07E6 |  | 22nd harmonic content | WORD
| 2023 | 0X07E7 |  | 23rd harmonic content | WORD
| 2024 | 0X07E8 |  | 24th harmonic content | WORD
| 2025 | 0X07E9 |  | 25th harmonic content | WORD
| 2026 | 0X07EA |  | 26th harmonic content | WORD
| 2027 | 0X07EB |  | 27th harmonic content | WORD
| 2028 | 0X07EC |  | 28th harmonic content | WORD
| 2029 | 0X07ED |  | 29th harmonic content | WORD
| 2030 | 0X07EE |  | 30th harmonic content | WORD
| 2031 | 0X07EF |  | 31st harmonic content | WORD
| 2032 | 0X07F0 | Voltage Ib harmonic content | 0 harmonic content | WORD
| 2033 | 0X07F1 |  | 1st harmonic content | WORD
| 2034 | 0X07F2 |  | 2nd harmonic content | WORD
| 2035 | 0X07F3 |  | 3rd harmonic content | WORD
| 2036 | 0X07F4 |  | 4th harmonic content | WORD
| 2037 | 0X07F5 |  | 5th harmonic content | WORD
| 2038 | 0X07F6 |  | 6th harmonic content | WORD
| 2039 | 0X07F7 |  | 7th harmonic content | WORD
| 2040 | 0X07F8 |  | 8th harmonic content | WORD
| 2041 | 0X07F9 |  | 9th harmonic content | WORD
| 2042 | 0X07FA |  | 10th harmonic content | WORD
| 2043 | 0X07FB |  | 11st harmonic content | WORD
| 2044 | 0X07FC |  | 12nd harmonic content | WORD
| 2045 | 0X07FD |  | 13rd harmonic content | WORD
| 2046 | 0X07FE |  | 14th harmonic content | WORD
| 2047 | 0X07FF |  | 15th harmonic content | WORD
| 2048 | 0X0800 |  | 16th harmonic content | WORD
| 2049 | 0X0801 |  | 17th harmonic content | WORD
| 2050 | 0X0802 |  | 18th harmonic content | WORD
| 2051 | 0X0803 |  | 19th harmonic content | WORD
| 2052 | 0X0804 |  | 20th harmonic content | WORD
| 2053 | 0X0805 |  | 21st harmonic content | WORD
| 2054 | 0X0806 |  | 22nd harmonic content | WORD
| 2055 | 0X0807 |  | 23rd harmonic content | WORD
| 2056 | 0X0808 |  | 24th harmonic content | WORD
| 2057 | 0X0809 |  | 25th harmonic content | WORD
| 2058 | 0X080A |  | 26th harmonic content | WORD
| 2059 | 0X080B |  | 27th harmonic content | WORD
| 2060 | 0X080C |  | 28th harmonic content | WORD
| 2061 | 0X080D |  | 29th harmonic content | WORD
| 2062 | 0X080E |  | 30th harmonic content | WORD
| 2063 | 0X080F |  | 31st harmonic content | WORD
| 2064 | 0X0810 | Voltage Ic harmonic content | 0 harmonic content | WORD
| 2065 | 0X0811 |  | 1st harmonic content | WORD
| 2066 | 0X0812 |  | 2nd harmonic content | WORD
| 2067 | 0X0813 |  | 3rd harmonic content | WORD
| 2068 | 0X0814 |  | 4th harmonic content | WORD
| 2069 | 0X0815 |  | 5th harmonic content | WORD
| 2070 | 0X0816 |  | 6th harmonic content | WORD
| 2071 | 0X0817 |  | 7th harmonic content | WORD
| 2072 | 0X0818 |  | 8th harmonic content | WORD
| 2073 | 0X0819 |  | 9th harmonic content | WORD
| 2074 | 0X081A |  | 10th harmonic content | WORD
| 2075 | 0X081B |  | 11st harmonic content | WORD
| 2076 | 0X081C |  | 12nd harmonic content | WORD
| 2077 | 0X081D |  | 13rd harmonic content | WORD
| 2078 | 0X081E |  | 14th harmonic content | WORD
| 2079 | 0X081F |  | 15th harmonic content | WORD
| 2080 | 0X0820 |  | 16th harmonic content | WORD
| 2081 | 0X0821 |  | 17th harmonic content | WORD
| 2082 | 0X0822 |  | 18th harmonic content | WORD
| 2083 | 0X0823 |  | 19th harmonic content | WORD
| 2084 | 0X0824 |  | 20th harmonic content | WORD
| 2085 | 0X0825 |  | 21st harmonic content | WORD
| 2086 | 0X0826 |  | 22nd harmonic content | WORD
| 2087 | 0X0827 |  | 23rd harmonic content | WORD
| 2088 | 0X0828 |  | 24th harmonic content | WORD
| 2089 | 0X0829 |  | 25th harmonic content | WORD
| 2090 | 0X082A |  | 26th harmonic content | WORD
| 2091 | 0X082B |  | 27th harmonic content | WORD
| 2092 | 0X082C |  | 28th harmonic content | WORD
| 2093 | 0X082D |  | 29th harmonic content | WORD
| 2094 | 0X082E |  | 30th harmonic content | WORD
| 2095 | 0X082F |  | 31st harmonic content | WORD

## Sheet 3
Protection Action Even Record（Function Code 03 Read）
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Format | Remark
256 | 0X0100 | Action Value-1 | Protection 1 Action Value | WORD | Remark 2
257 | 0X0101 | Action Value--1A | Protection 1 Action Value (A Phase) | WORD | Remark 3
258 | 0X0102 | Action Value--1B | Protection 1 Action Value (B Phase) | WORD
259 | 0X0103 | Action Value--1C | Protection 1 Action Value (C Phase) | WORD
260 | 0X0104 | Setting Value--1 | Protection 1 Setting Value | WORD | Remark 4
261 | 0X0105 | Year-1 | Action 1 Time-Year | High BYTE | Remark 5
|  | Mon-1 | Action 1 Time-Month | Low BYTE
262 | 0X0106 | Day-1 | Action 1 Time-Day | High BYTE
|  | Hour-1 | Action 1 Time-Hour | Low BYTE
263 | 0X0107 | Minute-1 | Action 1 Time-Minute | High BYTE
|  | Second-1 | Action 1 Time-Second | Low BYTE
264 | 0X0108 | Millisecond-1 | Action 1 Time-Millisecond | WORD | 0~999
265 | 0X0100 | Action Value-2 | Protection 2 Action Value | WORD
266 | 0X0101 | Action Value-2A | Protection 2 Action Value (A Phase) | WORD
267 | 0X0102 | Action Value-2B | Protection 2 Action Value (B Phase) | WORD
268 | 0X0103 | Action Value-2C | Protection 2 Action Value (C Phase) | WORD
269 | 0X0104 | Setting Value-2 | Protection 2 Setting Value | WORD
270 | 0X0105 | Year-2 | Action 2 Time-Year | High BYTE
|  | Mon-2 | Action 2 Time-Month | Low BYTE
271 | 0X0106 | Day-2 | Action 2 Time-Day | High BYTE
|  | Hour-2 | Action 2 Time-Hour | Low BYTE
272 | 0X0107 | Minute-2 | Action 2 Time-Minute | High BYTE
|  | Second-2 | Action 2 Time-Second | Low BYTE
273 | 0X0108 | Millisecond-2 | Action 2 Time-Millisecond | WORD | 0~999
......(Total 32 groups)
535 | 0X0217 | Action Value-32 | Protection 32 Action Value | WORD
536 | 0X0218 | Action Value-32A | Protection 32 Action Value (A Phase) | WORD
537 | 0X0219 | Action Value-32B | Protection 32 Action Value (B Phase) | WORD
538 | 0X021A | Action Value-32C | Protection 32 Action Value (C Phase) | WORD
539 | 0X021B | Setting Value-32 | Protection 32 Setting Value | WORD
540 | 0X021C | Year-32 | Action 32 Time-Year | High BYTE
|  | Mon-32 | Action 32 Time-Month | Low BYTE
541 | 0X021D | Day-32 | Action 32 Time-Day | High BYTE
|  | Hour-32 | Action 32 Time-Hour | Low BYTE
542 | 0X021E | Minute-32 | Action 32 Time-Minute | High BYTE
|  | Second-32 | Action 32 Time-Second | Low BYTE
543 | 0X021F | Millisecond-32 | Action 32 Time-Millisecond | WORD | 0~999
Remark：1、Alarm Indictor：
No | Address | Flag Bit | Fault Signal | Active Virtual Value | Format | Instruction
1 | 0X000A | Bit0 | Over Current | 1 | Bit
2 | 0X000A | Bit1 | Over Voltage | 1 | Bit
3 | 0X000A | Bit2 | under voltage | 1 | Bit
4 | 0X000A | Bit3 | Phase Loss | 1 | Bit
5 | 0X000A | Bit4 | Unblance | 1 | Bit
6 | 0X000A | Bit5 | Blank | 1 | Bit
7 | 0X000A | Bit6 | Blank | 1 | Bit
8 | 0X000A | Bit7 | Blank | 1 | Bit
9 | 0X000A | Bit8 | Blank | 1 | Bit
10 | 0X000A | Bit9 | Blank | 1 | Bit
11 | 0X000A | Bit10 | Blank | 1 | Bit
12 | 0X000A | Bit11 | Blank | 1 | Bit
13 | 0X000A | Bit12 | Blank | 1 | Bit
14 | 0X000A | Bit13 | Blank | 1 | Bit
15 | 0X000A | Bit14 | Blank | 1 | Bit
16 | 0X000A | Bit15 | Total Bland | 1 | Bit
After reading the SOE records, please clear this register value.
Remark：2、SOE Action：
No | Flag Bit | Type | Active Virtual Value | Format | Instruction
1 | Bit0 | Over Current | 1 | Bit
2 | Bit1 | Over Voltage | 1 | Bit
3 | Bit2 | under voltage | 1 | Bit
4 | Bit3 | Phase Loss | 1 | Bit
5 | Bit4 | Unblance | 1 | Bit
6 | Bit5 | Blank | 1 | Bit
7 | Bit6 | Blank | 1 | Bit
8 | Bit7 | DI1 Connection | 1 | Bit
9 | Bit8 | DI1 Disconnection | 1 | Bit
10 | Bit9 | DI2 Connection | 1 | Bit
11 | Bit10 | DI2 Disconnection | 1 | Bit
12 | Bit11 | Clear Energy | 1 | Bit
13 | Bit12 | Modify Parameter | 1 | Bit
14 | Bit13 | Blank | 1 | Bit
15 | Bit14 | Blank | 1 | Bit
16 | Bit15 | Blank | 1 | Bit
Remark：3、SOE Action： The following three SOE, the action registers won't save the value. (1)DI statue changed；(2)Clear energy value；(3)Modify parameters.
Remark：4、SOE Setting Value： The setting value is the overshoot threshold. Eg：if the voltage value is over the threshold value, it will alarm
Remark：5、SOE Action Time： 1、Binarycoded Decima。 Eg：July 2013：0X1306 10am 26th：0X2610 12m50s：0X1250

## Sheet 4
Electrical Data（200points of each cycle）（Function Code: 03/04 read)
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Format | Remark
4096 | 0x1000 | Current value in a stroke | Point 1 IB Current Value | WORD
4097 | 0x1001 |  | Point 2 IB Current Value | WORD
4098 | 0x1002 |  | Point 3 IB Current Value | WORD
4099 | 0x1003 |  | Point 4 IB Current Value | WORD
…… | …… |  | …… | WORD
…… | …… |  | …… | WORD
…… | …… |  | …… | WORD
4293 | 0x10C5 |  | Point 198 IB Current Value | WORD
4294 | 0x10C6 |  | Point 199 IB Current Value | WORD
4295 | 0x10C7 |  | Point 200 IB Current Value | WORD
4296 | 0x10C8 | Instantaneous value of active power in a stroke | Point 1 Active Power Value | Signed WORD
4297 | 0x10C9 |  | Point 2 Active Power Value | Signed WORD
4298 | 0x10CA |  | Point 3 Active Power Value | Signed WORD
4299 | 0x10CB |  | Point 4 Active Power Value | Signed WORD
…… | …… |  | …… | Signed WORD
…… | …… |  | …… | Signed WORD
…… | …… |  | …… | Signed WORD
4493 | 0x118D |  | Point 198 Active Power Value | Signed WORD
4494 | 0x118E |  | Point 199 Active Power Value | Signed WORD
4495 | 0x118F |  | Point 200 Active Power Value | Signed WORD
4496 | 0x1190 |  | energy metering time—Year | High BYTE
|  |  | energy metering time—Month | Low BYTE
4497 | 0x1191 |  | energy metering time—Day | High BYTE
|  |  | energy metering time—Hour | Low BYTE
4498 | 0x1192 |  | energy metering time—Mintuts | High BYTE
|  |  | energy metering time—Second | Low BYTE

## Sheet 5
Basic Setting：（Function Code : 0X06 or 0X10 write; Function Code: 03 read）
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Format | Remark
114 | 0X0072 | Time | Device Running Time-High Bit | WORD | Unit：Hour
115 | 0X0073 |  | Device Running Time-Low Bit | WORD | Revertible
128 | 0X0080 | Addr | Device Commnuication Address | WORD
129 | 0X0081 | Baud | Baund Rate | WORD
130 | 0X0082 | VOLT | PT Ratio | WORD
131 | 0X0083 | ALPE | CT Ratio | WORD
132 | 0X0084 | POTV | Voltage decimal point position | High BYTE | （Remark A）
|  | POTA | Current decimal point position | Low BYTE | （Remark A）
133 | 0X0085 | POTP | Blank | High BYTE
|  |  | Power decimal point position | Low BYTE | （Remark A）
134 | 0x0086 | MODE | Wiring & Power Direction Option | High BYTE | （Remark B）
|  |  | Display Mode | Low BYTE | （Remark C）
135 | 0X0087 | Ed- U | Motor Rated Voltage Ue | WORD | decimal point position is the same with that of voltage
136 | 0X0088 | Ed- A | Motor Rated Current Ie | WORD | decimal point position is the same with that of current
137 | 0X0089 | RST | Automatic resetting time | WORD
138 | 0X008A | eniba | Blank | High BYTE
|  |  | protection enable,1 refers to the protection is valid | Low BYTE | （Remark D）
139 | 0X008B | Trips | Blank | High BYTE
|  |  | output is tripping mode | Low BYTE | （Remark F）
140 | 0X008C | RELY | Relay output mode （1: pluse，elctric level） | High BYTE | （Remark G）
|  |  | Time value of pulse length （10-250）Unit is 0.1 second | Low BYTE
141 | 0X008D | PASS | Meter Password | WORD
142 | 0X008E | KYZ | Energy Pulse Constant | WORD
143 | 0X008F | MaxT | NC | High BYTE
|  |  | Demand Cycle | Low BYTE | Unit:minute
144 | 0X0090 | HI-I | E/H+“over current”setting value [105%~200%]Ie | High BYTE
|  |  | P/L+Overcurrent action time limit（Grade difference is 0.1s）[0.1~25.0 s] | Low BYTE
145 | 0X0091 | HI-V | action setting value of motor "overvoltage" [105%~200%]Ue | High BYTE
|  |  | Overvoltage action time limit（Grade difference is 0.1s）[0.1~25.0 s] | Low BYTE
146 | 0X0092 | LO-V | action setting value of motor "undeervoltage"[20%~100%]Ue | High BYTE
|  |  | Undervoltage action time limit（Grade difference is 0.1s）[ 0.1~25.0 s] | Low BYTE
147 | 0X0093 | LOST | E/H+motor current loss phase | High BYTE
|  |  | P/L+loss phase action time limit（Grade difference is 0.1s）[0.1~25.0 s] | Low BYTE
148 | 0X0094 | BRED | E/H+motor current "unblance"setting percent[10%~95%] | High BYTE
|  |  | P/L+unblande action time limit（Grade difference is 0.1s）[0.1~25.0 s] | Low BYTE
149 | 0X0095 | HI-Io | "Zero Sequence Overcurrent" Setting Value Range of Motor [30%～100%]Ie | High BYTE
|  |  | Zero Sequence Overflow Operation Time Limit （Grade difference is 0.1s）[0.1s～25.0s] | Low BYTE
150 | 0X0096 | HI-Uo | "Zero-sequence Overvoltage" Setting Value Range of Motor [30%～100%]Ue | High BYTE
|  |  | Zero sequence overvoltage action time limit （Grade difference is 0.1s）[0.1s～25.0s] | Low BYTE
*Remark B：wiring mode & power direction option
Bit15 | Bit14 | Bit13 | Bit12 | Bit11 | Bit10 | Bit9 | Bit8
0 | R-MOD | 0 | F-FF | 0 | 0 | 0 | J_X
Bit12（F_FF）is 0 refers to the power & energy metering is no direction, if the value is 1, that means the metering is import &export power & energy. Bit8（J_X）is 0 refers to 3Phse4Wire，if it is 0, that means the wring is the 3phase3wire
*Remark C：Display Mode： Cyclic display（0x22）；Key switch display（0x00）
*Remark D：E/H protection enable, 1: the protection action is valid
Bit7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0
| Zero sequence overvoltage | Zero sequence overcurrent | Unblance | Loss Phase | Under Voltage | Overvoltage | Overcurrent
*Renark E：“0” is Modbus RTU prtocol，others are the IEC 101 protocol.
*Remark F：1: alarm and trip, 0:only alarm without tripping
Bit7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0
|  |  | Unblance | Loss Phase | Under Voltage | Overvoltage | Overcurrent
*Remark G：Relay Output（1 byte）：
Bit15 | Bit14 | Bit13 | Bit12 | Bit11 | Bit10 | Bit9 | Bit8
0 | 0 | 0 | 0 | 0 | 0 | OUT2 | OUT1
If the corresponding Bit is 1, that means it is the pluse output mode, otherwise, if the bit is 0, that means it is the elctric level mode. Eg：the value of Bit9 is 1,that means the relay output2（OUT2）is the pluse output mode. the value of Bit8 is 0，that means the relay output1（OUT1）is the electric level mode.

## Sheet 6
Multi-tariff Period Setting：（Function Code : 0X06 or 0X10 write; Function Code: 03 read）
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Format | Remark
160 | 0x00A0 | TIMEH1 | Start Time of The 1st Period: Hour | BYTE | High BYTE
|  |  | Start Time of The 1st Period: Minute | BYTE | Low BYTE
161 | 0x00A1 | TIMEL1 | End Time of The 1st Period: Hour | BYTE | High BYTE
|  |  | End Time of The 1st Period: Minute | BYTE | Low BYTE
162 | 0x00A2 | KIND1 | Blank | BYTE | High BYTE
|  |  | Tariff Type of The 1st Period Energy | BYTE | Low BYTE
163 | 0x00A3 | TIMEH2 | Start Time of The 2nd Period: Hour | BYTE | High BYTE
|  |  | Start Time of The 2nd Period: Minute | BYTE | Low BYTE
164 | 0x00A4 | TIMEL2 | End Time of The 2nd Period: Hour | BYTE | High BYTE
|  |  | End Time of The 2nd Period: Minute | BYTE | Low BYTE
165 | 0x00A5 | KIND2 | Blank | BYTE | High BYTE
|  |  | Tariff Type of The 2nd Period Energy | BYTE | Low BYTE
166 | 0x00A6 | TIMEH3 | Start Time of The 3rd Period: Hour | BYTE | High BYTE
|  |  | Start Time of The 3rd Period: Minute | BYTE | Low BYTE
167 | 0x00A7 | TIMEL3 | End Time of The 3rd Period: Hour | BYTE | High BYTE
|  |  | End Time of The 3rd Period: Minute | BYTE | Low BYTE
168 | 0x00A8 | KIND3 | Blank | BYTE | High BYTE
|  |  | Tariff Type of The 3rd Period Energy | BYTE | Low BYTE
169 | 0x00A9 | TIMEH4 | Start Time of The 4th Period: Hour | BYTE | High BYTE
|  |  | Start Time of The 4th Period: Minute | BYTE | Low BYTE
170 | 0x00AA | TIMEL4 | End Time of The 4th Period: Hour | BYTE | High BYTE
|  |  | End Time of The 4th Period: Minute | BYTE | Low BYTE
171 | 0x00AB | KIND4 | Blank | BYTE | High BYTE
|  |  | Tariff Type of The 4th Period Energy | BYTE | Low BYTE
172 | 0x00AC | TIMEH5 | Start Time of The 5th Period: Hour | BYTE | High BYTE
|  |  | Start Time of The 5th Period: Minute | BYTE | Low BYTE
173 | 0x00AD | TIMEL5 | End Time of The 5th Period: Hour | BYTE | High BYTE
|  |  | End Time of The 5th Period: Minute | BYTE | Low BYTE
174 | 0x00AE | KIND5 | Blank | BYTE | High BYTE
|  |  | Tariff Type of The 5th Period Energy | BYTE | Low BYTE
175 | 0x 00AF | TIMEH6 | Start Time of The 6th Period: Hour | BYTE | High BYTE
|  |  | Start Time of The 6th Period: Minute | BYTE | Low BYTE
176 | 0x00B0 | TIMEL6 | End Time of The 6th Period: Hour | BYTE | High BYTE
|  |  | End Time of The 6th Period: Minute | BYTE | Low BYTE
177 | 0x00B1 | KIND6 | Blank | BYTE | High BYTE
|  |  | Tariff Type of The 6th Period Energy | BYTE | Low BYTE
178 | 0x00B2 | TIMEH7 | Start Time of The 7th Period: Hour | BYTE | High BYTE
|  |  | Start Time of The 7th Period: Minute | BYTE | Low BYTE
179 | 0x00B3 | TIMEL7 | End Time of The 7th Period: Hour | BYTE | High BYTE
|  |  | End Time of The 7th Period: Minute | BYTE | Low BYTE
180 | 0x 00B4 | KIND7 | Blank | BYTE | High BYTE
|  |  | Tariff Type of The 7th Period Energy | BYTE | Low BYTE
181 | 0x00B5 | TIMEH8 | Start Time of The 8th Period: Hour | BYTE | High BYTE
|  |  | Start Time of The 8th Period: Minute | BYTE | Low BYTE
182 | 0x00B6 | TIMEL8 | End Time of The 8th Period: Hour | BYTE | High BYTE
|  |  | End Time of The 8th Period: Minute | BYTE | Low BYTE
183 | 0x00B7 | KIND8 | Blank | BYTE | High BYTE
|  |  | Tariff Type of The 8th Period Energy | BYTE | Low BYTE
184 | 0x00B8 | TIMEH9 | Start Time of The 9th Period: Hour | BYTE | High BYTE
|  |  | Start Time of The 9th Period: Minute | BYTE | Low BYTE
185 | 0x00B9 | TIMEL9 | End Time of The 9th Period: Hour | BYTE | High BYTE
|  |  | End Time of The 9th Period: Minute | BYTE | Low BYTE
186 | 0x00BA | KIND9 | Blank | BYTE | High BYTE
|  |  | Tariff Type of The 9th Period Energy | BYTE | Low BYTE
187 | 0x00BB | TIMEH10 | Start Time of The 10th Period: Hour | BYTE | High BYTE
|  |  | Start Time of The 10th Period: Minute | BYTE | Low BYTE
188 | 0x00BC | TIMEL10 | End Time of The 10th Period: Hour | BYTE | High BYTE
|  |  | End Time of The 10th Period: Minute | BYTE | Low BYTE
189 | 0x00BD | KIND10 | Blank | BYTE | High BYTE
|  |  | Tariff Type of The 10th Period Energy | BYTE | Low BYTE
Time Format is Hexadecimal 0x1603: 16hour 03 minute Tariff Type：0x01：Sharp 0x02：Peark 0x03：Off-peark 0x04：Shoulder The dafault setting is the off-peak period.

## Sheet 7
Electircal Parameters（Function Code 03/04 Read）
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Format | Remark
1536 | 0x0600 |  | Alarm Statue | WORD
1537 | 0x0601 |  | Alarm Value-Total three phase | WORD
1538 | 0x0602 |  | Alarm Value- A phase | WORD
1539 | 0x0603 |  | Alarm Value- B phase | WORD
1540 | 0x0604 |  | Alarm Value- C phase | WORD
1541 | 0x0605 |  | Alarm Incador | WORD
1542 | 0x0606 |  | Valid Value of Phase A Current | WORD
1543 | 0x0607 |  | Valid Value of Phase B Current | WORD
1544 | 0x0608 |  | Valid Value of Phase C Current | WORD
1545 | 0x0609 |  | 3 phase unblance Voltage 3U0 | WORD
1546 | 0x060A |  | 3 phase unblance Current 3I0 | WORD
1547 | 0x060B |  | Valid Value of Phase A Voltage | WORD
1548 | 0x060C |  | Valid Value of Phase B Voltage | WORD
1549 | 0x060D |  | Valid Value of Phase C Voltage | WORD
1550 | 0x060E |  | Valid Value of Phase AB Voltage | WORD
1551 | 0x060F |  | Valid Value of Phase BC Voltage | WORD
1552 | 0x0610 |  | Valid Value of Phase CA Voltage | WORD
1553 | 0x0611 |  | Active Power | WORD
1554 | 0x0612 |  | Reactive Power | WORD
1555 | 0x0613 |  | apparent power | WORD
1556 | 0x0614 |  | power factor | WORD
1557 | 0x0615 |  | Cycle | WORD
1558 | 0x0616 |  | active power of phase A | WORD
1559 | 0x0617 |  | active power of phase B | WORD
1560 | 0x0618 |  | active power of phase C | WORD
1561 | 0x0619 |  | reactive power of phase A | WORD
1562 | 0x061A |  | reactive power of phase B | WORD
1563 | 0x061B |  | reactive power of phase C | WORD
1564 | 0x061C |  | apparent power of phase A | WORD
1565 | 0x061D |  | apparent power of phase B | WORD
1566 | 0x061E |  | apparent power of phase C | WORD
1567 | 0x061F |  | power factor of phase A | WORD
1568 | 0x0620 |  | power factor of phase B | WORD
1569 | 0x0621 |  | power factor of phase C | WORD
1570 | 0x0622 |  | Import Total Active Energy Value- High Bit | WORD
1571 | 0x0623 |  | Import Total Active Energy Value- Low Bit | WORD
1572 | 0x0624 |  | Import Total Active Energy Value in Sharp Period-High Bit | WORD
1573 | 0x0625 |  | Import Total Active Energy Value in Sharp Period-Low Bit | WORD
1574 | 0x0626 |  | Import Total Active Energy Value in Peak Period-High Bit | WORD
1575 | 0x0627 |  | Import Total Active Energy Value in Peak Period-Low Bit | WORD
1576 | 0x0628 |  | Import Total Active Energy Value in off-Peak Period-Low Bit | WORD
1577 | 0x0629 |  | Import Total Active Energy Value in off-Peak Period-Low Bit | WORD
1578 | 0x062A |  | Import Total Active Energy Value in Shoulder Period-Low Bit | WORD
1579 | 0x062B |  | Import Total Active Energy Value in Shoulder Period-Low Bit | WORD
1580 | 0x062C |  | Export Total Active Energy Value- High Bit | WORD
1581 | 0x062D |  | Export Total Active Energy Value- Low Bit | WORD
1582 | 0x062E |  | Export Total Active Energy Value in Sharp Period-High Bit | WORD
1583 | 0x062F |  | Export Total Active Energy Value in Sharp Period-Low Bit | WORD
1584 | 0x0630 |  | Export Total Active Energy Value in Peak Period-High Bit | WORD
1585 | 0x0631 |  | Export Total Active Energy Value in Peak Period-Low Bit | WORD
1586 | 0x0632 |  | Export Total Active Energy Value in off-Peak Period-Low Bit | WORD
1587 | 0x0633 |  | Export Total Active Energy Value in off-Peak Period-Low Bit | WORD
1588 | 0x0634 |  | Export Total Active Energy Value in Shoulder Period-Low Bit | WORD
1589 | 0x0635 |  | Export Total Active Energy Value in Shoulder Period-Low Bit | WORD
1590 | 0x0636 |  | Reserved | WORD
1591 | 0x0637 |  | Reserved | WORD
1592 | 0x0638 |  | Reserved | WORD
1593 | 0x0639 |  | Reserved | WORD
1594 | 0x063A |  | Reserved | WORD
1595 | 0x063B |  | Reserved | WORD
1596 | 0x063C |  | Reserved | WORD
1597 | 0x063D |  | Reserved | WORD
1598 | 0x063E |  | Reserved | WORD
1599 | 0x063F |  | Reserved | WORD
1600 | 0x0640 |  | Reserved | 2ASCII
1601 | 0x0641 |  | Reserved | 2ASCII
1602 | 0x0642 |  | Reserved | 2ASCII
1603 | 0x0643 |  | Reserved | 2ASCII
1604 | 0x0644 |  | Reserved | 2ASCII
1605-1607 | 0x0645~0x0647 |  | Reserved | 6ASCII
1608 | 0x0648 |  | Reserved | 2ASCII
1609-1610 | 0x0649~0x064A |  | Reserved | 4ASCII
1611 | 0X064B |  | Reserved | 2ASCII
1612 | 0x064C |  | Device Communication Address | WORD
1613 | 0x064D |  | Baund Rate | WORD
1614 | 0x064E |  | PT Ratio | WORD
1615 | 0x064F |  | CT Ratio | WORD
1616 | 0x0650 |  | Current decimal point position | WORD
1617 | 0x0651 |  | Power decimal point position | WORD
1618 | 0x0652 |  | Wiring & Power Direction Option & Display | WORD
1619 | 0x0653 |  | Motor Rated Voltage Un | WORD
1620 | 0x0654 |  | Motor Rated Current In | WORD
1621 | 0x0655 |  | zero sequence | WORD
1622 | 0x0656 |  | Protection Enabling Mark | WORD
1623 | 0x0657 |  | Outpput Mode OPtion | WORD
1624 | 0x0658 |  | Relay Output | WORD
1625 | 0x0659 |  | Meter Password | WORD
1626 | 0x065A |  | Energy Pulse Constant | WORD
1627 | 0x065B |  | Demand Cycle | WORD
1628 | 0x065C |  | E/H+“over current”setting value [105%~200%]Ie | High BYTE
|  |  | P/L+Overcurrent action time limit（Grade difference is 0.1s）[0.1~25.0 s] | Low BYTE
1629 | 0x065D |  | action setting value of motor "overvoltage" [105%~200%]Ue | High BYTE
|  |  | Overvoltage action time limit（Grade difference is 0.1s）[0.1~25.0 s] | Low BYTE
1630 | 0x065E |  | action setting value of motor "undeervoltage"[20%~100%]Ue | High BYTE
|  |  | Undervoltage action time limit（Grade difference is 0.1s）[ 0.1~25.0 s] | Low BYTE
1631 | 0x065F |  | E/H+motor current loss phase | High BYTE
|  |  | P/L+loss phase action time limit（Grade difference is 0.1s）[0.1~25.0 s] | Low BYTE
1632 | 0x0660 |  | E/H+motor current "unblance"setting percent[10%~95%] | High BYTE
|  |  | P/L+unblande action time limit（Grade difference is 0.1s）[0.1~25.0 s] | Low BYTE
1633 | 0x0661 |  | "Zero Sequence Overcurrent" Setting Value Range of Motor [30%～100%]Ie | High BYTE
|  |  | Zero Sequence Overflow Operation Time Limit （Grade difference is 0.1s）[0.1s～25.0s] | Low BYTE
1634 | 0x0662 |  | "Zero-sequence Overvoltage" Setting Value Range of Motor [30%～100%]Ue | High BYTE
|  |  | Zero sequence overvoltage action time limit （Grade difference is 0.1s）[0.1s～25.0s] | Low BYTE
1635 | 0x0663 |  | Reserved
1636 | 0x0664 |  | Reserved
1637 | 0x0665 |  | Reserved
1638 | 0x0666 |  | Reserved
1639 | 0x0667 |  | Reserved
1640 | 0x0668 |  | Reserved
1641 | 0x0669 |  | Reserved
1642 | 0x066A |  | Sampling Points of Power Diagram | WORD
1643-1644 | 0x066B-0x066C |  | Cycle of Power Diagram | 2 WORD
1645 | 0x066D |  | Reserved
1646 | 0x066E |  | Reserved
1647 | 0x066F |  | Reserved
1648 | 0x0670 | Multi-tariff Period Setting | Start Time of The 1st Period: Hour | High BYTE
|  |  | Start Time of The 1st Period: Minute | Low BYTE
1649 | 0x0671 |  | End Time of The 1st Period: Hour | High BYTE
|  |  | End Time of The 1st Period: Minute | Low BYTE
1650 | 0x0672 |  | Blank | High BYTE
|  |  | Tariff Type of The 1st Period Energy | Low BYTE
1651 | 0x0673 |  | Start Time of The 2nd Period: Hour | High BYTE
|  |  | Start Time of The 2nd Period: Minute | Low BYTE
1652 | 0x0674 |  | End Time of The 2nd Period: Hour | High BYTE
|  |  | End Time of The 2nd Period: Minute | Low BYTE
1653 | 0x0675 |  | Blank | High BYTE
|  |  | Tariff Type of The 2nd Period Energy | Low BYTE
1654 | 0x0676 |  | Start Time of The 3rd Period: Hour | High BYTE
|  |  | Start Time of The 3rd Period: Minute | Low BYTE
1655 | 0x0677 |  | End Time of The 3rd Period: Hour | High BYTE
|  |  | End Time of The 3rd Period: Minute | Low BYTE
1656 | 0x0678 |  | Blank | High BYTE
|  |  | Tariff Type of The 3rd Period Energy | Low BYTE
1657 | 0x0679 |  | Start Time of The 4th Period: Hour | High BYTE
|  |  | Start Time of The 4th Period: Minute | Low BYTE
1658 | 0x067A |  | End Time of The 4th Period: Hour | High BYTE
|  |  | End Time of The 4th Period: Minute | Low BYTE
1659 | 0x067B |  | Blank | High BYTE
|  |  | Tariff Type of The 4th Period Energy | Low BYTE
1660 | 0x067C |  | Start Time of The 5th Period: Hour | High BYTE
|  |  | Start Time of The 5th Period: Minute | Low BYTE
1661 | 0x067D |  | End Time of The 5th Period: Hour | High BYTE
|  |  | End Time of The 5th Period: Minute | Low BYTE
1662 | 0x067E |  | Blank | High BYTE
|  |  | Tariff Type of The 5th Period Energy | Low BYTE
1663 | 0x067F |  | Start Time of The 6th Period: Hour | High BYTE
|  |  | Start Time of The 6th Period: Minute | Low BYTE
1664 | 0x0680 |  | End Time of The 6th Period: Hour | High BYTE
|  |  | End Time of The 6th Period: Minute | Low BYTE
1665 | 0x0681 |  | Blank | High BYTE
|  |  | Tariff Type of The 6th Period Energy | Low BYTE
1666 | 0x0682 |  | Start Time of The 7th Period: Hour | High BYTE
|  |  | Start Time of The 7th Period: Minute | Low BYTE
1667 | 0x0683 |  | End Time of The 7th Period: Hour | High BYTE
|  |  | End Time of The 7th Period: Minute | Low BYTE
1668 | 0x0684 |  | Blank | High BYTE
|  |  | Tariff Type of The 7th Period Energy | Low BYTE
1669 | 0x0685 |  | Start Time of The 8th Period: Hour | High BYTE
|  |  | Start Time of The 8th Period: Minute | Low BYTE
1670 | 0x0686 |  | End Time of The 8th Period: Hour | High BYTE
|  |  | End Time of The 8th Period: Minute | Low BYTE
1671 | 0x0687 |  | Blank | High BYTE
|  |  | Tariff Type of The 8th Period Energy | Low BYTE
1672 | 0x0688 |  | Start Time of The 9th Period: Hour | High BYTE
|  |  | Start Time of The 9th Period: Minute | Low BYTE
1673 | 0x0689 |  | End Time of The 9th Period: Hour | High BYTE
|  |  | End Time of The 9th Period: Minute | Low BYTE
1674 | 0x068A |  | Blank | High BYTE
|  |  | Tariff Type of The 9th Period Energy | Low BYTE
1675 | 0x068B |  | Start Time of The 10th Period: Hour | High BYTE
|  |  | Start Time of The 10th Period: Minute | Low BYTE
1676 | 0x068C |  | End Time of The 10th Period: Hour | High BYTE
|  |  | End Time of The 10th Period: Minute | Low BYTE
1677 | 0x068D |  | Blank | High BYTE
|  |  | Tariff Type of The 10th Period Energy | Low BYTE