## Read Only Zone
Item | Parameters | Display Format | Modbus Address | Register Type | Remark
(Hexadecimal)
1 | Total Combined Active Energy | xxxxxx.xx | 0x100 | Read Only | 0.01kWh Negative number as complement
0x101
2 | Combined Active Energy in Sharp period | xxxxxx.xx | 0x102 | Read Only
0x103
3 | Combined Active Energy in Peak period | xxxxxx.xx | 0x104 | Read Only
0x105
4 | Combined Active Energy Off-peak period | xxxxxx.xx | 0x106 | Read Only
0x107
5 | Combined Active Energy in Shoulder period | xxxxxx.xx | 0x108 | Read Only
0x109
6 | Total Import Active Energy | xxxxxx.xx | 0x10A | Read Only | 0.01kWh (Hexadecimal)
0x10B
7 | Import Active Energy in Sharp Period | xxxxxx.xx | 0x10C | Read Only
0x10D
8 | Import Active Energy in Peak Period | xxxxxx.xx | 0x10E | Read Only
0x10F
9 | Import Active Energy in off-peak Period | xxxxxx.xx | 0x110 | Read Only
0x111
10 | Import Active Energy in Shoulder Period | xxxxxx.xx | 0x112 | Read Only
0x113
11 | Total Export Active Energy | xxxxxx.xx | 0x114 | Read Only
0x115
12 | Export Active Energy in Sharp Period | xxxxxx.xx | 0x116 | Read Only
0x117
13 | Export Active Energy in Peak Period | xxxxxx.xx | 0x118 | Read Only
0x119
14 | Export Active Energy in off-peak Period | xxxxxx.xx | 0x11A | Read Only
0x11B
15 | Export Active Energy in Shoulder Period | xxxxxx.xx | 0x11C | Read Only
0x11D
16 | Total Combined Reactive 1 Energy | xxxxxx.xx | 0x11E | Read Only | 0.01kvarh Negative number as complement
0x11F
17 | Combined Reactive 1 Energy in Sharp period | xxxxxx.xx | 0x120 | Read Only
0x121
18 | Combined Reactive 1 Energy in Peak period | xxxxxx.xx | 0x122 | Read Only
0x123
19 | Combined Reactive 1 Energy Off-peak period | xxxxxx.xx | 0x124 | Read Only
0x125
20 | Combined Reactive 1 Energy in Shoulder period | xxxxxx.xx | 0x126 | Read Only
0x127
21 | Total Combined Reactive 2 Energy | xxxxxx.xx | 0x128 | Read Only
0x129
22 | Combined Reactive 2 Energy in Sharp period | xxxxxx.xx | 0x12A | Read Only
0x12B
23 | Combined Reactive 2 Energy in Peak period | xxxxxx.xx | 0x12C | Read Only
0x12D
24 | Combined Reactive 2 Energy Off-peak period | xxxxxx.xx | 0x12E | Read Only
0x12F
25 | Combined Reactive 2 Energy in Shoulder period | xxxxxx.xx | 0x130 | Read Only
0x131
26 | Total Energy of 1-quadrant | xxxxxx.xx | 0x132 | Read Only | 0.01kvarh (Hexadecimal)
0x133
27 | Sharp-period 1-quadrant Energy | xxxxxx.xx | 0x134 | Read Only
0x135
28 | Peak-period 1-quadrant Energy | xxxxxx.xx | 0x136 | Read Only
0x137
29 | Off-peak-period 1-quadrant Energy | xxxxxx.xx | 0x138 | Read Only
0x139
30 | Shoulder-period 1-quadrant Energy | xxxxxx.xx | 0x13A | Read Only
0x13B
31 | Total Energy of 2-quadrant | xxxxxx.xx | 0x13C | Read Only
0x13D
32 | Sharp-period 2-quadrant Energy | xxxxxx.xx | 0x13E | Read Only
0x13F
33 | Peak-period 2-quadrant Energy | xxxxxx.xx | 0x140 | Read Only
0x141
34 | Off-peak-period 2-quadrant Energy | xxxxxx.xx | 0x142 | Read Only
0x143
35 | Shoulder-period 2-quadrant Energy | xxxxxx.xx | 0x144 | Read Only
0x145
36 | Total Energy of 3-quadrant | xxxxxx.xx | 0x146 | Read Only
0x147
37 | Sharp-period 3-quadrant Energy | xxxxxx.xx | 0x148 | Read Only
0x149
38 | Peak-period 3-quadrant Energy | xxxxxx.xx | 0x14A | Read Only
0x14B
39 | Off-peak-period 3-quadrant Energy | xxxxxx.xx | 0x14C | Read Only
0x14D
40 | Shoulder-period 3-quadrant Energy | xxxxxx.xx | 0x14E | Read Only
0x14F
41 | Total Energy of 4-quadrant | xxxxxx.xx | 0x150 | Read Only
0x151
42 | Sharp-period 4-quadrant Energy | xxxxxx.xx | 0x152 | Read Only
0x153
43 | Peak-period 4-quadrant Energy | xxxxxx.xx | 0x154 | Read Only
0x155
44 | Off-peak-period 4-quadrant Energy | xxxxxx.xx | 0x156 | Read Only
0x157
45 | Shoulder-period 4-quadrant Energy | xxxxxx.xx | 0x158 | Read Only
0x159
46 | Total Import Apparent Energy | xxxxxx.xx | 0x15A | Read Only | 0.01kVAh (Hexadecimal)
0x15B
47 | Import Apparent Energy in Sharp period | xxxxxx.xx | 0x15C | Read Only
0x15D
48 | Import Apparent Energy in Peak period | xxxxxx.xx | 0x15E | Read Only
0x15F
49 | Import Apparent Energy Off-peak period | xxxxxx.xx | 0x160 | Read Only
0x161
50 | Import Apparent Energy in Shoulder period | xxxxxx.xx | 0x162 | Read Only
0x163
51 | Total Export Apparent Energy | xxxxxx.xx | 0x164 | Read Only
0x165
52 | Export Apparent Energy in Sharp period | xxxxxx.xx | 0x166 | Read Only
0x167
53 | Export Apparent Energy in Peak period | xxxxxx.xx | 0x168 | Read Only
0x169
54 | Export Apparent Energy Off-peak period | xxxxxx.xx | 0x16A | Read Only
0x16B
55 | Export Apparent Energy in Shoulder period | xxxxxx.xx | 0x16C | Read Only
0x16D
56 | Phase A Voltage | xxxx.xxx | 0x16E | Read Only | 0.0001V (Hexadecimal)
0x16F
57 | Phase B Voltage | xxxx.xxx | 0x170 | Read Only
0x171
58 | Phase C Voltage | xxxx.xxx | 0x172 | Read Only
0x173
59 | Phase A Current | xxxx.xxx | 0x174 | Read Only | 0.0001A (Hexadecimal)
0x175
60 | Phase B Current | xxxx.xxx | 0x176 | Read Only
0x177
61 | Phase C Current | xxxx.xxx | 0x178 | Read Only
0x179
62 | Real-time Total Active Power | xxxx.xxx | 0x17A | Read Only | 0.0001kW, Hexadecimal, Negative number as complement
0x17B
63 | Active Power of Phase A | xxxx.xxx | 0x17C | Read Only
0x17D
64 | Active Power of Phase B | xxxx.xxx | 0x17E | Read Only
0x17F
65 | Active Power of Phase C | xxxx.xxx | 0x180 | Read Only
0x181
66 | Real-time Total Reactive Power | xxxx.xxx | 0x182 | Read Only | 0.0001kvar, Hexadecimal, Negative number as complement
0x183
67 | Reactive Power of Phase A | xxxx.xxx | 0x184 | Read Only
0x185
68 | Reactive Power of Phase B | xxxx.xxx | 0x186 | Read Only
0x187
69 | Reactive Power of Phase C | xxxx.xxx | 0x188 | Read Only
0x189
70 | Real-time Total Apparent Power | xxxx.xxx | 0x18A | Read Only | 0.0001kVA, Hexadecimal
0x18B
71 | Apparent Power of Phase A | xxxx.xxx | 0x18C | Read Only
0x18D
72 | Apparent Power of Phase B | xxxx.xxx | 0x18E | Read Only
0x18F
73 | Apparent Power of Phase C | xxxx.xxx | 0x190 | Read Only
0x191
74 | Total Power Factor | x.xxx | 0x192 | Read Only | 0.001, Hexadecimal, Negative number as complement
75 | Power Factor of Phase A | x.xxx | 0x193 | Read Only
76 | Power Factor of Phase B | x.xxx | 0x194 | Read Only
77 | Power Factor of Phase C | x.xxx | 0x195 | Read Only
78 | Phase A Degree | xxx.x | 0x196 | Read Only | 0.1°, Hexadecimal,
79 | Phase B Degree | xxx.x | 0x197 | Read Only
80 | Phase C Degree | xxx.x | 0x198 | Read Only
81 | Frequency | xx.xx | 0x199 | Read Only | 0.01Hz, Hexadecimal

## kWh, U, I, P, PF, F
Item | Parameters | Circuit | Display Format | Modbus Address | Register Type | Remark
(Hexadecimal)
1 | Combined Active Energy | 1st | xxxxxx.xx | 0x1000 | Read Only | kWh (Hexadecimal) Negative number as complement
0x1001
2 |  | 2nd | xxxxxx.xx | 0x1002 | Read Only
0x1003
3 |  | 3rd | xxxxxx.xx | 0x1004 | Read Only
0x1005
4 |  | 4th | xxxxxx.xx | 0x1006 | Read Only
0x1007
5 | Import Active Energy | 1st | xxxxxx.xx | 0x1030 | Read Only | kWh (Hexadecimal)
0x1031
6 |  | 2nd | xxxxxx.xx | 0x1032 | Read Only
0x1033
7 |  | 3rd | xxxxxx.xx | 0x1034 | Read Only
0x1035
8 |  | 4th | xxxxxx.xx | 0x1036 | Read Only
0x1037
9 | Export Active Energy | 1st | xxxxxx.xx | 0x1060 | Read Only | kWh (Hexadecimal)
0x1061
10 |  | 2nd | xxxxxx.xx | 0x1062 | Read Only
0x1063
11 |  | 3rd | xxxxxx.xx | 0x1064 | Read Only
0x1065
12 |  | 4th | xxxxxx.xx | 0x1066 | Read Only
0x1067
13 | Phase A Voltage | 1st | xxxx.xxxx | 0x1090 | Read Only | V (Hexadecimal)
0x1091
14 | Phase B Voltage | 1st | xxxx.xxxx | 0x1092 | Read Only
0x1093
15 | Phase C Voltage | 1st | xxxx.xxxx | 0x1094 | Read Only
0x1095
16 | Phase A Voltage | 2nd | xxxx.xxxx | 0x1096 | Read Only
0x1097
17 | Phase B Voltage | 2nd | xxxx.xxxx | 0x1098 | Read Only
0x1099
18 | Phase C Voltage | 2nd | xxxx.xxxx | 0x109A | Read Only
0x109B
19 | Phase A Voltage | 3rd | xxxx.xxxx | 0x109C | Read Only
0x109D
20 | Phase B Voltage | 3rd | xxxx.xxxx | 0x109E | Read Only
0x109F
21 | Phase C Voltage | 3rd | xxxx.xxxx | 0x10A0 | Read Only
0x10A1
22 | Phase A Voltage | 4th | xxxx.xxxx | 0x10A2 | Read Only
0x10A3
23 | Phase B Voltage | 4th | xxxx.xxxx | 0x10A4 | Read Only
0x10A5
24 | Phase C Voltage | 4th | xxxx.xxxx | 0x10A6 | Read Only
0x10A7
25 | Phase A Current | 1st | xxxx.xxxx | 0x10C0 | Read Only | A (Hexadecimal)
0x10C1
26 | Phase B Current | 1st | xxxx.xxxx | 0x10C2 | Read Only
0x10C3
27 | Phase C Current | 1st | xxxx.xxxx | 0x10C4 | Read Only
0x10C5
28 | Phase A Current | 2nd | xxxx.xxxx | 0x10C6 | Read Only
0x10C7
29 | Phase B Current | 2nd | xxxx.xxxx | 0x10C8 | Read Only
0x10C9
30 | Phase C Current | 2nd | xxxx.xxxx | 0x10CA | Read Only
0x10CB
31 | Phase A Current | 3rd | xxxx.xxxx | 0x10CC | Read Only | A (Hexadecimal)
0x10CD
32 | Phase B Current | 3rd | xxxx.xxxx | 0x10CE | Read Only
0x10CF
33 | Phase C Current | 3rd | xxxx.xxxx | 0x10D0 | Read Only
0x10D1
34 | Phase A Current | 4th | xxxx.xxxx | 0x10D2 | Read Only
0x10D3
35 | Phase B Current | 4th | xxxx.xxxx | 0x10D4 | Read Only
0x10D5
36 | Phase C Current | 4th | xxxx.xxxx | 0x10D6 | Read Only
0x10D7
37 | Total Active Power | 1st | xx.xxxx | 0x1100 | Read Only | kW (Hexadecimal) Negative number as complement
0x1101
38 | Active Power of Phase A | 1st | xx.xxxx | 0x1102 | Read Only
0x1103
39 | Active Power of Phase B | 1st | xx.xxxx | 0x1104 | Read Only
0x1105
40 | Active Power of Phase C | 1st | xx.xxxx | 0x1106 | Read Only
0x1107
41 | Total Active Power | 2nd | xx.xxxx | 0x1108 | Read Only
0x1109
42 | Active Power of Phase A | 2nd | xx.xxxx | 0x110A | Read Only
0x110B
43 | Active Power of Phase B | 2nd | xx.xxxx | 0x110C | Read Only
0x110D
44 | Active Power of Phase C | 2nd | xx.xxxx | 0x110E | Read Only
0x110F
45 | Total Active Power | 3rd | xx.xxxx | 0x1110 | Read Only
0x1111
46 | Active Power of Phase A | 3rd | xx.xxxx | 0x1112 | Read Only
0x1113
47 | Active Power of Phase B | 3rd | xx.xxxx | 0x1114 | Read Only
0x1115
48 | Active Power of Phase C | 3rd | xx.xxxx | 0x1116 | Read Only
0x1117
49 | Total Active Power | 4th | xx.xxxx | 0x1118 | Read Only | kW (Hexadecimal) Negative number as complement
0x1119
50 | Active Power of Phase A | 4th | xx.xxxx | 0x111A | Read Only
0x111B
51 | Active Power of Phase B | 4th | xx.xxxx | 0x111C | Read Only
0x111D
52 | Active Power of Phase C | 4th | xx.xxxx | 0x111E | Read Only
0x111F
53 | Total Reactive Power | 1st | xx.xxxx | 0x1140 | Read Only | kvar (Hexadecimal) Negative number as complement
0x1141
54 | Reactive Power of Phase A | 1st | xx.xxxx | 0x1142 | Read Only
0x1143
55 | Reactive Power of Phase B | 1st | xx.xxxx | 0x1144 | Read Only
0x1145
56 | Reactive Power of Phase C | 1st | xx.xxxx | 0x1146 | Read Only
0x1147
57 | Total Reactive Power | 2nd | xx.xxxx | 0x1148 | Read Only
0x1149
58 | Reactive Power of Phase A | 2nd | xx.xxxx | 0x114A | Read Only
0x114B
59 | Reactive Power of Phase B | 2nd | xx.xxxx | 0x114C | Read Only
0x114D
60 | Reactive Power of Phase C | 2nd | xx.xxxx | 0x114E | Read Only
0x114F
61 | Total Reactive Power | 3rd | xx.xxxx | 0x1150 | Read Only | kvar (Hexadecimal) Negative number as complement
0x1151
62 | Reactive Power of Phase A | 3rd | xx.xxxx | 0x1152 | Read Only
0x1153
63 | Reactive Power of Phase B | 3rd | xx.xxxx | 0x1154 | Read Only
0x1155
64 | Reactive Power of Phase C | 3rd | xx.xxxx | 0x1156 | Read Only
0x1157
65 | Total Reactive Power | 4th | xx.xxxx | 0x1158 | Read Only
0x1159
66 | Reactive Power of Phase A |  | xx.xxxx | 0x115A | Read Only
0x115B
67 | Reactive Power of Phase B |  | xx.xxxx | 0x115C | Read Only
0x115D
68 | Reactive Power of Phase C |  | xx.xxxx | 0x115E | Read Only
0x115F
69 | Total Power Factor | 1st | x.xxx | 0x1190 | Read Only | (Hexadecimal) Negative number as complement
70 | Power Factor of Phase A |  | x.xxx | 0x1191 | Read Only
71 | Power Factor of Phase B |  | x.xxx | 0x1192 | Read Only
72 | Power Factor of Phase C |  | x.xxx | 0x1193 | Read Only
73 | Total Power Factor | 2st | x.xxx | 0x1194 | Read Only
74 | Power Factor of Phase A |  | x.xxx | 0x1195 | Read Only
75 | Power Factor of Phase B |  | x.xxx | 0x1196 | Read Only
76 | Power Factor of Phase C |  | x.xxx | 0x1197 | Read Only
77 | Total Power Factor | 3st | x.xxx | 0x1198 | Read Only
78 | Power Factor of Phase A |  | x.xxx | 0x1199 | Read Only
79 | Power Factor of Phase B |  | x.xxx | 0x119A | Read Only
80 | Power Factor of Phase C |  | x.xxx | 0x119B | Read Only
81 | Total Power Factor | 4st | x.xxx | 0x119C | Read Only
82 | Power Factor of Phase A |  | x.xxx | 0x119D | Read Only
83 | Power Factor of Phase B |  | x.xxx | 0x119E | Read Only
84 | Power Factor of Phase C |  | x.xxx | 0x119F | Read Only
85 | Frequency | 1st | xx.xx | 0x11B0 | Read Only | Hz (Hexadecimal)
86 |  | 2st | xx.xx | 0x11B1
87 |  | 3st | xx.xx | 0x11B2
88 |  | 4st | xx.xx | 0x11B3

## THD
Item | Parameters | Display Format | Modbus Address | Register Type | Remark
(Hexadecimal)
1 | 1st Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11E1 | Read Only | Hexadecimal
2 | 2nd Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11E2 | Read Only | Hexadecimal
3 | 3rd Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11E3 | Read Only | Hexadecimal
4 | 4th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11E4 | Read Only | Hexadecimal
5 | 5th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11E5 | Read Only | Hexadecimal
6 | 6th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11E6 | Read Only | Hexadecimal
7 | 7th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11E7 | Read Only | Hexadecimal
8 | 8th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11E8 | Read Only | Hexadecimal
9 | 9th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11E9 | Read Only | Hexadecimal
10 | 10th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11EA | Read Only | Hexadecimal
11 | 11th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11EB | Read Only | Hexadecimal
12 | 12th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11EC | Read Only | Hexadecimal
13 | 13th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11ED | Read Only | Hexadecimal
14 | 14th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11EE | Read Only | Hexadecimal
15 | 15th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11EF | Read Only | Hexadecimal
16 | 16th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11F0 | Read Only | Hexadecimal
17 | 17th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11F1 | Read Only | Hexadecimal
18 | 18th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11F2 | Read Only | Hexadecimal
19 | 19th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11F3 | Read Only | Hexadecimal
20 | 20th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11F4 | Read Only | Hexadecimal
21 | 21th Phase A voltage harmonic content of 1 circuit | xx.xx | 0x11F5 | Read Only | Hexadecimal
22 | 1st Phase B voltage harmonic content of 1 circuit | xx.xx | 0x11F6 | Read Only | Hexadecimal
23 | 2nd Phase B voltage harmonic content of 1 circuit | xx.xx | 0x11F7 | Read Only | Hexadecimal
24 | 3rd Phase B voltage harmonic content of 1 circuit | xx.xx | 0x11F8 | Read Only | Hexadecimal
25 | 4th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x11F9 | Read Only | Hexadecimal
26 | 5th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x11FA | Read Only | Hexadecimal
27 | 6th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x11FB | Read Only | Hexadecimal
28 | 7th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x11FC | Read Only | Hexadecimal
29 | 8th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x11FD | Read Only | Hexadecimal
30 | 9th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x11FE | Read Only | Hexadecimal
31 | 10th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x11FF | Read Only | Hexadecimal
32 | 11th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x1200 | Read Only | Hexadecimal
33 | 12th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x1201 | Read Only | Hexadecimal
34 | 13th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x1202 | Read Only | Hexadecimal
35 | 14th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x1203 | Read Only | Hexadecimal
36 | 15th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x1204 | Read Only | Hexadecimal
37 | 16th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x1205 | Read Only | Hexadecimal
38 | 17th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x1206 | Read Only | Hexadecimal
39 | 18th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x1207 | Read Only | Hexadecimal
40 | 19th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x1208 | Read Only | Hexadecimal
41 | 20th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x1209 | Read Only | Hexadecimal
42 | 21th Phase B voltage harmonic content of 1 circuit | xx.xx | 0x120A | Read Only | Hexadecimal
43 | 1st Phase C voltage harmonic content of 1 circuit | xx.xx | 0x120B | Read Only | Hexadecimal
44 | 2nd Phase C voltage harmonic content of 1 circuit | xx.xx | 0x120C | Read Only | Hexadecimal
45 | 3rd Phase C voltage harmonic content of 1 circuit | xx.xx | 0x120D | Read Only | Hexadecimal
46 | 4th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x120E | Read Only | Hexadecimal
47 | 5th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x120F | Read Only | Hexadecimal
48 | 6th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x1210 | Read Only | Hexadecimal
49 | 7th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x1211 | Read Only | Hexadecimal
50 | 8th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x1212 | Read Only | Hexadecimal
51 | 9th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x1213 | Read Only | Hexadecimal
52 | 10th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x1214 | Read Only | Hexadecimal
53 | 11th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x1215 | Read Only | Hexadecimal
54 | 12th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x1216 | Read Only | Hexadecimal
55 | 13th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x1217 | Read Only | Hexadecimal
56 | 14th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x1218 | Read Only | Hexadecimal
57 | 15th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x1219 | Read Only | Hexadecimal
58 | 16th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x121A | Read Only | Hexadecimal
59 | 17th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x121B | Read Only | Hexadecimal
60 | 18th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x121C | Read Only | Hexadecimal
61 | 19th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x121D | Read Only | Hexadecimal
62 | 20th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x121E | Read Only | Hexadecimal
63 | 21th Phase C voltage harmonic content of 1 circuit | xx.xx | 0x121F | Read Only | Hexadecimal
64 | 1st~21th Phase A voltage harmonic content of 2 circuit | xx.xx | 0x1220~0x1234 | Read Only | Hexadecimal
65 | 1st~21th Phase B voltage harmonic content of 2 circuit | xx.xx | 0x1235~0x1249 | Read Only | Hexadecimal
66 | 1st~21th Phase C voltage harmonic content of 2 circuit | xx.xx | 0x124A~0x125E | Read Only | Hexadecimal
67 | 1st~21th Phase A voltage harmonic content of 3 circuit | xx.xx | 0x125F~0x1273 | Read Only | Hexadecimal
68 | 1st~21th Phase B voltage harmonic content of 3 circuit | xx.xx | 0x1274~0x1288 | Read Only | Hexadecimal
69 | 1st~21th Phase C voltage harmonic content of 3 circuit | xx.xx | 0x1289~0x129D | Read Only | Hexadecimal
70 | 1st~21th Phase A voltage harmonic content of 4 circuit | xx.xx | 0x129E~0x12B2 | Read Only | Hexadecimal
71 | 1st~21th Phase B voltage harmonic content of 4 circuit | xx.xx | 0x12B3~0x12C7 | Read Only | Hexadecimal
72 | 1st~21th Phase C voltage harmonic content of 4 circuit | xx.xx | 0x12C8~0x12DC | Read Only | Hexadecimal
73 | 1st~21th Phase A current harmonic content of 1 circuit | xx.xx | 0x12E0~0x12F4 | Read Only | Hexadecimal
74 | 1st~21th Phase B current harmonic content of 1 circuit | xx.xx | 0x12F5~0x1309 | Read Only | Hexadecimal
75 | 1st~21th Phase C current harmonic content of 1 circuit | xx.xx | 0x130A~0x131E | Read Only | Hexadecimal
76 | 1st~21th Phase A current harmonic content of 2 circuit | xx.xx | 0x131F~0x1333 | Read Only | Hexadecimal
77 | 1st~21th Phase B current harmonic content of 2 circuit | xx.xx | 0x1334~0x1348 | Read Only | Hexadecimal
78 | 1st~21th Phase C current harmonic content of 2 circuit | xx.xx | 0x1349~0x135D | Read Only | Hexadecimal
79 | 1st~21th Phase A current harmonic content of 3 circuit | xx.xx | 0x135E~0x1372 | Read Only | Hexadecimal
80 | 1st~21th Phase B current harmonic content of 3 circuit | xx.xx | 0x1373~0x1387 | Read Only | Hexadecimal
81 | 1st~21th Phase C current harmonic content of 3 circuit | xx.xx | 0x1388~0x139C | Read Only | Hexadecimal
82 | 1st~21th Phase A current harmonic content of 4 circuit | xx.xx | 0x139D~0x13B1 | Read Only | Hexadecimal
83 | 1st~21th Phase B current harmonic content of 4 circuit | xx.xx | 0x13B2~0x13C6 | Read Only | Hexadecimal
84 | 1st~21th Phase C current harmonic content of 4 circuit | xx.xx | 0x13C7~0x13DB | Read Only | Hexadecimal

## kvar·h, kVA·h
Item | Parameters | Display Format | Modbus Address |  | Register Type | Remark
|  |  | (Hexadecimal) | (Decimal)
1 | Combined Reactive Energy 1 of 1st circuit | xxxxxx.xx | 0x13E0 | 5088 | Read Only | 0.01kvar·h (Hexadecimal)
|  | xxxxxx.xx | 0x13E1 | 5089 | Read Only | 0.01kvar·h (Hexadecimal)
2 | Combined Reactive Energy 1 of 2nd circuit | xxxxxx.xx | 0x13E2 | 5090 | Read Only | 0.01kvar·h (Hexadecimal)
|  | xxxxxx.xx | 0x13E3 | 5091 | Read Only | 0.01kvar·h (Hexadecimal)
3 | Combined Reactive Energy 1 of 3rd circuit | xxxxxx.xx | 0x13E4 | 5092 | Read Only | 0.01kvar·h (Hexadecimal)
|  | xxxxxx.xx | 0x13E5 | 5093 | Read Only | 0.01kvar·h (Hexadecimal)
4 | Combined Reactive Energy 1 of 4th circuit | xxxxxx.xx | 0x13E6 | 5094 | Read Only | 0.01kvar·h (Hexadecimal)
|  | xxxxxx.xx | 0x13E7 | 5095 | Read Only | 0.01kvar·h (Hexadecimal)
5 | Combined Reactive Energy 2 of 1st circuit | xxxxxx.xx | 0x1410 | 5136 | Read Only | 0.01kvar·h (Hexadecimal)
|  | xxxxxx.xx | 0x1411 | 5137 | Read Only | 0.01kvar·h (Hexadecimal)
6 | Combined Reactive Energy 2 of 2nd circuit | xxxxxx.xx | 0x1412 | 5138 | Read Only | 0.01kvar·h (Hexadecimal)
|  | xxxxxx.xx | 0x1413 | 5139 | Read Only | 0.01kvar·h (Hexadecimal)
7 | Combined Reactive Energy 2 of 3rd circuit | xxxxxx.xx | 0x1414 | 5140 | Read Only | 0.01kvar·h (Hexadecimal)
|  | xxxxxx.xx | 0x1415 | 5141 | Read Only | 0.01kvar·h (Hexadecimal)
8 | Combined Reactive Energy 2 of 4th circuit | xxxxxx.xx | 0x1416 | 5142 | Read Only | 0.01kvar·h (Hexadecimal)
|  | xxxxxx.xx | 0x1417 | 5143 | Read Only | 0.01kvar·h (Hexadecimal)
9 | Import Apparent Energy of 1st circuit | xxxxxx.xx | 0x1440 | 5184 | Read Only | 0.01kVA·h (Hexadecimal)
|  | xxxxxx.xx | 0x1441 | 5185 | Read Only | 0.01kVA·h (Hexadecimal)
10 | Import Apparent Energy of 2nd circuit | xxxxxx.xx | 0x1442 | 5186 | Read Only | 0.01kVA·h (Hexadecimal)
|  | xxxxxx.xx | 0x1443 | 5187 | Read Only | 0.01kVA·h (Hexadecimal)
11 | Import Apparent Energy of 3rd circuit | xxxxxx.xx | 0x1444 | 5188 | Read Only | 0.01kVA·h (Hexadecimal)
|  | xxxxxx.xx | 0x1445 | 5189 | Read Only | 0.01kVA·h (Hexadecimal)
12 | Import Apparent Energy of 4th circuit | xxxxxx.xx | 0x1446 | 5190 | Read Only | 0.01kVA·h (Hexadecimal)
|  | xxxxxx.xx | 0x1447 | 5191 | Read Only | 0.01kVA·h (Hexadecimal)
13 | Export Apparent Energy of 1st circuit | xxxxxx.xx | 0x1470 | 5232 | Read Only | 0.01kVA·h (Hexadecimal)
|  | xxxxxx.xx | 0x1471 | 5233 | Read Only | 0.01kVA·h (Hexadecimal)
14 | Export Apparent Energy of 2nd circuit | xxxxxx.xx | 0x1472 | 5234 | Read Only | 0.01kVA·h (Hexadecimal)
|  | xxxxxx.xx | 0x1473 | 5235 | Read Only | 0.01kVA·h (Hexadecimal)
15 | Export Apparent Energy of 3rd circuit | xxxxxx.xx | 0x1474 | 5236 | Read Only | 0.01kVA·h (Hexadecimal)
|  | xxxxxx.xx | 0x1475 | 5237 | Read Only | 0.01kVA·h (Hexadecimal)
16 | Export Apparent Energy of 4th circuit | xxxxxx.xx | 0x1476 | 5238 | Read Only | 0.01kVA·h (Hexadecimal)
|  | xxxxxx.xx | 0x1477 | 5239 | Read Only | 0.01kVA·h (Hexadecimal)

## Read and Write Zone
Item | Parameters | Modbus Address | Register Type | Remark
(Hexadecimal)
1 | Second | 0x00 | Read/Write | Decimal
2 | Minute | 0x01 | Read/Write | Decimal
3 | Hour | 0x02 | Read/Write | Decimal
4 | Week | 0x03 | Read/Write | Decimal
5 | Day | 0x04 | Read/Write | Decimal
6 | Month | 0x05 | Read/Write | Decimal
7 | Year | 0x06 | Read/Write | Decimal
8 | Communication Address | 0x07 | Read/Write | Hexadecimal
9 | Reserve | 0x08 | Read/Write | Hexadecimal
10 | PT Ratio | 0x09 | Read/Write | Hexadecimal
11 | CT Ratio | 0x0A | Read/Write | Hexadecimal
12 | Baud Rate (0x04:1200; 0x8:2400; 0x10:4800; 0x20:9600, 0x40:19200) | 0x64 | Read/Write | Hexadecimal
13 | Zero Energy (0000) | 0x11E0 | Write | Hexadecimal