## Basic Parameter
►Remark: Formulas Between True Values and Modbus Registers' Values U(true value)=Register*PT/100 （unit:V） I(true value)=Register*CT/10000 （unit:A） P(true value)=Register*PT*CT/100 （unit:W）(single phase) P(true value)=Register*PT*CT/10 （unit:W）(total three phase phase) Q(true value)=Register*PT*CT/100 （unit:VAr）(single phase) Q(true value)=Register*PT*CT/10 （unit:VAr）(total three phase phase) S(true value)=Register*PT*CT/100 （unit:VA）(single phase) S(true value)=Register*PT*CT/10 （unit:VA）(total three phase phase) PF(true value)=Register/1000
Basically Measured Parameters Zone （Holding Register Model No.03/Input Register Model No.04）
| Address |  | Single Phase Circuit | Three Phase Circuit | Parameters | Default | Value Range
| (Decimal) | (hexadecimal)
1 | 4096 | 1000 | Total Voltage |  | phase A voltage | magnifying 100 times | 0～65535
2 | 4097 | 1001 |  |  | phase B voltage | magnifying 100 times | 0～65535
3 | 4098 | 1002 |  |  | phase C voltage | magnifying 100 times | 0～65535
4 | 4099 | 1003 |  |  | phase voltage mean value | magnifying 100 times | 0～65535
5 | 4100 | 1004 |  |  | zero sequence voltage | magnifying 100 times | 0～65535
6 | 4101 | 1005 | Loop 1 Current | Loop 1 | Phase A Current | magnifying 10000 times | 0～65535
7 | 4102 | 1006 | Loop 2 Current |  | Phase B Current | magnifying 10000 times | 0～65535
8 | 4103 | 1007 | Loop 3 Current |  | Phase C Current | magnifying 10000 times | 0～65536
9 | 4104 | 1008 | / |  | Zero Phase Current | magnifying 10000 times | 0～65535
10 | 4105 | 1009 | Loop 1 Active Power |  | Phase A Active Power | magnifying 100 times | -32768～32767
11 | 4106 | 100A | Loop 2 Active Power |  | Phase B Active Power | magnifying 100 times | -32768～32767
12 | 4107 | 100B | Loop 3 Active Power |  | Phase C Active Power | magnifying 100 times | -32768～32768
13 | 4108 | 100C | / |  | Total three-phase active power | magnifying 10 times | -32768～32767
14 | 4109 | 100D | Loop 1 Reactive Power |  | Phase A Reactive Power | magnifying 100 times | -32768～32767
15 | 4110 | 100E | Loop 2 Reactive Power |  | Phase B Reactive Power | magnifying 100 times | -32768～32767
16 | 4111 | 100F | Loop 3 Reactive Power |  | Phase C Reactive Power | magnifying 100 times | -32768～32767
17 | 4112 | 1010 | / |  | Total three-phase reactive power | magnifying 10 times | -32768～32767
18 | 4113 | 1011 | Loop 1 Apparent Power |  | Phase A Apparent Power | magnifying 100 times | -32768～32767
19 | 4114 | 1012 | Loop 2 Apparent Power |  | Phase B Apparent Power | magnifying 100 times | -32768～32767
20 | 4115 | 1013 | Loop 3 Apparent Power |  | Phase C Apparent Power | magnifying 100 times | -32768～32768
21 | 4116 | 1014 | / |  | Total three-phase apparent power | magnifying 10 times | -32768～32767
22 | 4117 | 1015 | Loop 1 Power Factor |  | Phase A Power Factor | magnifying 1000 times | -1000～1000
23 | 4118 | 1016 | Loop 2 Power Factor |  | Phase B Power Factor | magnifying 1000 times | -1000～1000
24 | 4119 | 1017 | Loop 3 Power Factor |  | Phase C Power Factor | magnifying 1000 times | -1000～1000
25 | 4120 | 1018 | / |  | Total three-phase power factor | magnifying 1000 times | -1000～1000
26 | 4121 | 1019 | Loop 4 Current | Loop 2 | Phase A Current | magnifying 10000 times | 0～65535
27 | 4122 | 101A | Loop 5 Current |  | Phase B Current | magnifying 10000 times | 0～65535
28 | 4123 | 101B | Loop 6 Current |  | Phase C Current | magnifying 10000 times | 0～65536
29 | 4124 | 101C | / |  | Zero Phase Current | magnifying 10000 times | 0～65535
30 | 4125 | 101D | Loop 4 Active Power |  | Phase A Active Power | magnifying 100 times | -32768～32767
31 | 4126 | 101E | Loop 5 Active Power |  | Phase B Active Power | magnifying 100 times | -32768～32767
32 | 4127 | 101F | Loop 6 Active Power |  | Phase C Active Power | magnifying 100 times | -32768～32768
33 | 4128 | 1020 | / |  | Total three-phase active power | magnifying 10 times | -32768～32767
34 | 4129 | 1021 | Loop 4 Reactive Power |  | Phase A Reactive Power | magnifying 100 times | -32768～32767
35 | 4130 | 1022 | Loop 5 Reactive Power |  | Phase B Reactive Power | magnifying 100 times | -32768～32767
36 | 4131 | 1023 | Loop 6 Reactive Power |  | Phase C Reactive Power | magnifying 100 times | -32768～32767
37 | 4132 | 1024 | / |  | Total three-phase reactive power | magnifying 10 times | -32768～32767
38 | 4133 | 1025 | Loop 4 Apparent Power |  | Phase A Apparent Power | magnifying 100 times | -32768～32767
39 | 4134 | 1026 | Loop 5 Apparent Power |  | Phase B Apparent Power | magnifying 100 times | -32768～32767
40 | 4135 | 1027 | Loop 6 Apparent Power |  | Phase C Apparent Power | magnifying 100 times | -32768～32768
41 | 4136 | 1028 | / |  | Total three-phase apparent power | magnifying 10 times | -32768～32767
42 | 4137 | 1029 | Loop 4 Power Factor |  | Phase A Power Factor | magnifying 1000 times | -1000～1000
43 | 4138 | 102A | Loop 5 Power Factor |  | Phase B Power Factor | magnifying 1000 times | -1000～1000
44 | 4139 | 102B | Loop 6 Power Factor |  | Phase C Power Factor | magnifying 1000 times | -1000～1000
45 | 4140 | 102C | / |  | Total three-phase power factor | magnifying 1000 times | -1000～1000
46 | 4141 | 102D | Loop 7 Current | Loop 3 | Phase A Current | magnifying 10000 times | 0～65535
47 | 4142 | 102E | Loop 8 Current |  | Phase B Current | magnifying 10000 times | 0～65535
48 | 4143 | 102F | Loop 9 Current |  | Phase C Current | magnifying 10000 times | 0～65536
49 | 4144 | 1030 | / |  | Zero Phase Current | magnifying 10000 times | 0～65535
50 | 4145 | 1031 | Loop 7 Active Power |  | Phase A Active Power | magnifying 100 times | -32768～32767
51 | 4146 | 1032 | Loop 8 Active Power |  | Phase B Active Power | magnifying 100 times | -32768～32767
52 | 4147 | 1033 | Loop 9 Active Power |  | Phase C Active Power | magnifying 100 times | -32768～32768
53 | 4148 | 1034 | / |  | Total three-phase active power | magnifying 10 times | -32768～32767
54 | 4149 | 1035 | Loop 7 Reactive Power |  | Phase A Reactive Power | magnifying 100 times | -32768～32767
55 | 4150 | 1036 | Loop 8 Reactive Power |  | Phase B Reactive Power | magnifying 100 times | -32768～32767
56 | 4151 | 1037 | Loop 9 Reactive Power |  | Phase C Reactive Power | magnifying 100 times | -32768～32767
57 | 4152 | 1038 | / |  | Total three-phase reactive power | magnifying 10 times | -32768～32767
58 | 4153 | 1039 | Loop 7 Apparent Power |  | Phase A Apparent Power | magnifying 100 times | -32768～32767
59 | 4154 | 103A | Loop 8 Apparent Power |  | Phase B Apparent Power | magnifying 100 times | -32768～32767
60 | 4155 | 103B | Loop 9 Apparent Power |  | Phase C Apparent Power | magnifying 100 times | -32768～32768
61 | 4156 | 103C | / |  | Total three-phase apparent power | magnifying 10 times | -32768～32767
62 | 4157 | 103D | Loop 7 Power Factor |  | Phase A Power Factor | magnifying 1000 times | -1000～1000
63 | 4158 | 103E | Loop 8 Power Factor |  | Phase B Power Factor | magnifying 1000 times | -1000～1000
64 | 4159 | 103F | Loop 9 Power Factor |  | Phase C Power Factor | magnifying 1000 times | -1000～1000
65 | 4160 | 1040 | / |  | Total three-phase power factor | magnifying 1000 times | -1000～1000
66 | 4161 | 1041 | Loop 10 Current | Loop 4 | Phase A Current | magnifying 10000 times | 0～65535
67 | 4162 | 1042 | Loop 11 Current |  | Phase B Current | magnifying 10000 times | 0～65535
68 | 4163 | 1043 | Loop 12 Current |  | Phase C Current | magnifying 10000 times | 0～65536
69 | 4164 | 1044 | / |  | Zero Phase Current | magnifying 10000 times | 0～65535
70 | 4165 | 1045 | Loop 10 Active Power |  | Phase A Active Power | magnifying 100 times | -32768～32767
71 | 4166 | 1046 | Loop 11 Active Power |  | Phase B Active Power | magnifying 100 times | -32768～32767
72 | 4167 | 1047 | Loop 12 Active Power |  | Phase C Active Power | magnifying 100 times | -32768～32768
73 | 4168 | 1048 | / |  | Total three-phase active power | magnifying 10 times | -32768～32767
74 | 4169 | 1049 | Loop 10 Reactive Power |  | Phase A Reactive Power | magnifying 100 times | -32768～32767
75 | 4170 | 104A | Loop 11 Reactive Power |  | Phase B Reactive Power | magnifying 100 times | -32768～32767
76 | 4171 | 104B | Loop 12 Reactive Power |  | Phase C Reactive Power | magnifying 100 times | -32768～32767
77 | 4172 | 104C | / |  | Total three-phase reactive power | magnifying 10 times | -32768～32767
78 | 4173 | 104D | Loop 10 Apparent Power |  | Phase A Apparent Power | magnifying 100 times | -32768～32767
79 | 4174 | 104E | Loop 11 Apparent Power |  | Phase B Apparent Power | magnifying 100 times | -32768～32767
80 | 4175 | 104F | Loop 12 Apparent Power |  | Phase C Apparent Power | magnifying 100 times | -32768～32768
81 | 4176 | 1050 | / |  | Total three-phase apparent power | magnifying 10 times | -32768～32767
82 | 4177 | 1051 | Loop 10 Power Factor |  | Phase A Power Factor | magnifying 1000 times | -1000～1000
83 | 4178 | 1052 | Loop 11 Power Factor |  | Phase B Power Factor | magnifying 1000 times | -1000～1000
84 | 4179 | 1053 | Loop 12 Power Factor |  | Phase C Power Factor | magnifying 1000 times | -1000～1000
85 | 4180 | 1054 | / |  | Total three-phase power factor | magnifying 1000 times | -1000～1000
86 | 4181 | 1055 | Loop 13 Current | Loop 5 | Phase A Current | magnifying 10000 times | 0～65535
87 | 4182 | 1056 | Loop 14 Current |  | Phase B Current | magnifying 10000 times | 0～65535
88 | 4183 | 1057 | Loop 15 Current |  | Phase C Current | magnifying 10000 times | 0～65536
89 | 4184 | 1058 | / |  | Zero Phase Current | magnifying 10000 times | 0～65535
90 | 4185 | 1059 | Loop 13 Active Power |  | Phase A Active Power | magnifying 100 times | -32768～32767
91 | 4186 | 105A | Loop 14 Active Power |  | Phase B Active Power | magnifying 100 times | -32768～32767
92 | 4187 | 105B | Loop 15 Active Power |  | Phase C Active Power | magnifying 100 times | -32768～32768
93 | 4188 | 105C | / |  | Total three-phase active power | magnifying 10 times | -32768～32767
94 | 4189 | 105D | Loop 13 Reactive Power |  | Phase A Reactive Power | magnifying 100 times | -32768～32767
95 | 4190 | 105E | Loop 14 Reactive Power |  | Phase B Reactive Power | magnifying 100 times | -32768～32767
96 | 4191 | 105F | Loop 15 Reactive Power |  | Phase C Reactive Power | magnifying 100 times | -32768～32767
97 | 4192 | 1060 | / |  | Total three-phase reactive power | magnifying 10 times | -32768～32767
98 | 4193 | 1061 | Loop 13 Apparent Power |  | Phase A Apparent Power | magnifying 100 times | -32768～32767
99 | 4194 | 1062 | Loop 14 Apparent Power |  | Phase B Apparent Power | magnifying 100 times | -32768～32767
100 | 4195 | 1063 | Loop 15 Apparent Power |  | Phase C Apparent Power | magnifying 100 times | -32768～32768
101 | 4196 | 1064 | / |  | Total three-phase apparent power | magnifying 10 times | -32768～32767
102 | 4197 | 1065 | Loop 13 Power Factor |  | Phase A Power Factor | magnifying 1000 times | -1000～1000
103 | 4198 | 1066 | Loop 14 Power Factor |  | Phase B Power Factor | magnifying 1000 times | -1000～1000
104 | 4199 | 1067 | Loop 15 Power Factor |  | Phase C Power Factor | magnifying 1000 times | -1000～1000
105 | 4200 | 1068 | / |  | Total three-phase power factor | magnifying 1000 times | -1000～1000
106 | 4201 | 1069 | Loop 16 Current | Loop 6 | Phase A Current | magnifying 10000 times | 0～65535
107 | 4202 | 106A | Loop 17 Current |  | Phase B Current | magnifying 10000 times | 0～65535
108 | 4203 | 106B | Loop 18 Current |  | Phase C Current | magnifying 10000 times | 0～65536
109 | 4204 | 106C | / |  | Zero Phase Current | magnifying 10000 times | 0～65535
110 | 4205 | 106D | Loop 16 Active Power |  | Phase A Active Power | magnifying 100 times | -32768～32767
111 | 4206 | 106E | Loop 17 Active Power |  | Phase B Active Power | magnifying 100 times | -32768～32767
112 | 4207 | 106F | Loop 18 Active Power |  | Phase C Active Power | magnifying 100 times | -32768～32768
113 | 4208 | 1070 | / |  | Total three-phase active power | magnifying 10 times | -32768～32767
114 | 4209 | 1071 | Loop 16 Reactive Power |  | Phase A Reactive Power | magnifying 100 times | -32768～32767
115 | 4210 | 1072 | Loop 17 Reactive Power |  | Phase B Reactive Power | magnifying 100 times | -32768～32767
116 | 4211 | 1073 | Loop 18 Reactive Power |  | Phase C Reactive Power | magnifying 100 times | -32768～32767
117 | 4212 | 1074 | / |  | Total three-phase reactive power | magnifying 10 times | -32768～32767
118 | 4213 | 1075 | Loop 16 Apparent Power |  | Phase A Apparent Power | magnifying 100 times | -32768～32767
119 | 4214 | 1076 | Loop 17 Apparent Power |  | Phase B Apparent Power | magnifying 100 times | -32768～32767
120 | 4215 | 1077 | Loop 18 Apparent Power |  | Phase C Apparent Power | magnifying 100 times | -32768～32768
121 | 4216 | 1078 | / |  | Total three-phase apparent power | magnifying 10 times | -32768～32767
122 | 4217 | 1079 | Loop 16 Power Factor |  | Phase A Power Factor | magnifying 1000 times | -1000～1000
123 | 4218 | 107A | Loop 17 Power Factor |  | Phase B Power Factor | magnifying 1000 times | -1000～1000
124 | 4219 | 107B | Loop 18 Power Factor |  | Phase C Power Factor | magnifying 1000 times | -1000～1000
125 | 4220 | 107C | / |  | Total three-phase power factor | magnifying 1000 times | -1000～1000
126 | 4221 | 107D | Loop 19 Current | Loop 7 | Phase A Current | magnifying 10000 times | 0～65535
127 | 4222 | 107E | Loop 20 Current |  | Phase B Current | magnifying 10000 times | 0～65535
128 | 4223 | 107F | Loop 21 Current |  | Phase C Current | magnifying 10000 times | 0～65536
129 | 4224 | 1080 | / |  | Zero Phase Current | magnifying 10000 times | 0～65535
130 | 4225 | 1081 | Loop 19 Active Power |  | Phase A Active Power | magnifying 100 times | -32768～32767
131 | 4226 | 1082 | Loop 20 Active Power |  | Phase B Active Power | magnifying 100 times | -32768～32767
132 | 4227 | 1083 | Loop 21 Active Power |  | Phase C Active Power | magnifying 100 times | -32768～32768
133 | 4228 | 1084 | / |  | Total three-phase active power | magnifying 10 times | -32768～32767
134 | 4229 | 1085 | Loop 19 Reactive Power |  | Phase A Reactive Power | magnifying 100 times | -32768～32767
135 | 4230 | 1086 | Loop 20 Reactive Power |  | Phase B Reactive Power | magnifying 100 times | -32768～32767
136 | 4231 | 1087 | Loop 21 Reactive Power |  | Phase C Reactive Power | magnifying 100 times | -32768～32767
137 | 4232 | 1088 | / |  | Total three-phase reactive power | magnifying 10 times | -32768～32767
138 | 4233 | 1089 | Loop 19 Apparent Power |  | Phase A Apparent Power | magnifying 100 times | -32768～32767
139 | 4234 | 108A | Loop 20 Apparent Power |  | Phase B Apparent Power | magnifying 100 times | -32768～32767
140 | 4235 | 108B | Loop 21 Apparent Power |  | Phase C Apparent Power | magnifying 100 times | -32768～32768
141 | 4236 | 108C | / |  | Total three-phase apparent power | magnifying 10 times | -32768～32767
142 | 4237 | 108D | Loop 19 Power Factor |  | Phase A Power Factor | magnifying 1000 times | -1000～1000
143 | 4238 | 108E | Loop 20 Power Factor |  | Phase B Power Factor | magnifying 1000 times | -1000～1000
144 | 4239 | 108F | Loop 21 Power Factor |  | Phase C Power Factor | magnifying 1000 times | -1000～1000
145 | 4240 | 1090 | / |  | Total three-phase power factor | magnifying 1000 times | -1000～1000
146 | 4241 | 1091 | Loop 22 Current | Loop 8 | Phase A Current | magnifying 10000 times | 0～65535
147 | 4242 | 1092 | Loop 23 Current |  | Phase B Current | magnifying 10000 times | 0～65535
148 | 4243 | 1093 | Loop 24 Current |  | Phase C Current | magnifying 10000 times | 0～65536
149 | 4244 | 1094 | / |  | Zero Phase Current | magnifying 10000 times | 0～65535
150 | 4245 | 1095 | Loop 22 Active Power |  | Phase A Active Power | magnifying 100 times | -32768～32767
151 | 4246 | 1096 | Loop 23 Active Power |  | Phase B Active Power | magnifying 100 times | -32768～32767
152 | 4247 | 1097 | Loop 24 Active Power |  | Phase C Active Power | magnifying 100 times | -32768～32768
153 | 4248 | 1098 | / |  | Total three-phase active power | magnifying 10 times | -32768～32767
154 | 4249 | 1099 | Loop 22 Reactive Power |  | Phase A Reactive Power | magnifying 100 times | -32768～32767
155 | 4250 | 109A | Loop 23 Reactive Power |  | Phase B Reactive Power | magnifying 100 times | -32768～32767
156 | 4251 | 109B | Loop 24 Reactive Power |  | Phase C Reactive Power | magnifying 100 times | -32768～32767
157 | 4252 | 109C | / |  | Total three-phase reactive power | magnifying 10 times | -32768～32767
158 | 4253 | 109D | Loop 22 Apparent Power |  | Phase A Apparent Power | magnifying 100 times | -32768～32767
159 | 4254 | 109E | Loop 23 Apparent Power |  | Phase B Apparent Power | magnifying 100 times | -32768～32767
160 | 4255 | 109F | Loop 24 Apparent Power |  | Phase C Apparent Power | magnifying 100 times | -32768～32768
161 | 4256 | 10A0 | / |  | Total three-phase apparent power | magnifying 10 times | -32768～32767
162 | 4257 | 10A1 | Loop 22 Power Factor |  | Phase A Power Factor | magnifying 1000 times | -1000～1000
163 | 4258 | 10A2 | Loop 23 Power Factor |  | Phase B Power Factor | magnifying 1000 times | -1000～1000
164 | 4259 | 10A3 | Loop 24 Power Factor |  | Phase C Power Factor | magnifying 1000 times | -1000～1000
165 | 4260 | 10A4 | / |  | Total three-phase power factor | magnifying 1000 times | -1000～1000
166 | 4261 | 10A5 | Loop 25 Current | Loop 9 | Phase A Current | magnifying 10000 times | 0～65535
167 | 4262 | 10A6 | Loop 26 Current |  | Phase B Current | magnifying 10000 times | 0～65535
168 | 4263 | 10A7 | Loop 27 Current |  | Phase C Current | magnifying 10000 times | 0～65536
169 | 4264 | 10A8 | / |  | Zero Phase Current | magnifying 10000 times | 0～65535
170 | 4265 | 10A9 | Loop 25 Active Power |  | Phase A Active Power | magnifying 100 times | -32768～32767
171 | 4266 | 10AA | Loop 26 Active Power |  | Phase B Active Power | magnifying 100 times | -32768～32767
172 | 4267 | 10AB | Loop 27 Active Power |  | Phase C Active Power | magnifying 100 times | -32768～32768
173 | 4268 | 10AC | / |  | Total three-phase active power | magnifying 10 times | -32768～32767
174 | 4269 | 10AD | Loop 25 Reactive Power |  | Phase A Reactive Power | magnifying 100 times | -32768～32767
175 | 4270 | 10AE | Loop 26 Reactive Power |  | Phase B Reactive Power | magnifying 100 times | -32768～32767
176 | 4271 | 10AF | Loop 27 Reactive Power |  | Phase C Reactive Power | magnifying 100 times | -32768～32767
177 | 4272 | 10B0 | / |  | Total three-phase reactive power | magnifying 10 times | -32768～32767
178 | 4273 | 10B1 | Loop 25 Apparent Power |  | Phase A Apparent Power | magnifying 100 times | -32768～32767
179 | 4274 | 10B2 | Loop 26 Apparent Power |  | Phase B Apparent Power | magnifying 100 times | -32768～32767
180 | 4275 | 10B3 | Loop 27 Apparent Power |  | Phase C Apparent Power | magnifying 100 times | -32768～32768
181 | 4276 | 10B4 | / |  | Total three-phase apparent power | magnifying 10 times | -32768～32767
182 | 4277 | 10B5 | Loop 25 Power Factor |  | Phase A Power Factor | magnifying 1000 times | -1000～1000
183 | 4278 | 10B6 | Loop 26 Power Factor |  | Phase B Power Factor | magnifying 1000 times | -1000～1000
184 | 4279 | 10B7 | Loop 27 Power Factor |  | Phase C Power Factor | magnifying 1000 times | -1000～1000
185 | 4280 | 10B8 | / |  | Total three-phase power factor | magnifying 1000 times | -1000～1000

## Energy Parameter(Real-time)
►Remark:Formulas Between True Values and Modbus Registers' Values Ep(True Value) =Register/100 （unit:kWh） Eq(True Value)=Register/100 （unit:kVArh)
| 9 Three phase circuits | [6 empty] | 27 Single phase circuits
| Address |  | Circuit | Parameter | Default Value | Value Range |  | Address |  | Circuit | Parameter | Default Value | Default Value
| (Decimal) | (Hexadecimal) | [5 empty] | (Decimal) | (Hexadecimal)
1 | 16384 | 4000 | Loop 1 | Total active energy | 0 | 0～9999999.99 | 1 | 16640 | 4100 | Loop 1 | Total active energy | 0 | 0～9999999.99
2 | 16385 | 4001 |  |  |  |  | 2 | 16641 | 4101
3 | 16386 | 4002 |  | Import Active Energy | 0 | 0～9999999.99 | 3 | 16642 | 4102 |  | Import active energy | 0 | 0～9999999.99
4 | 16387 | 4003 |  |  |  |  | 4 | 16643 | 4103
5 | 16388 | 4004 |  | Export Active Energy | 0 | 0～9999999.99 | 5 | 16644 | 4104 |  | Export active energy | 0 | 0～9999999.99
6 | 16389 | 4005 |  |  |  |  | 6 | 16645 | 4105
7 | 16390 | 4006 |  | Total reactive energy | 0 | 0～9999999.99 | 7 | 16646 | 4106 | Loop 2 | Total active energy | 0 | 0～9999999.99
8 | 16391 | 4007 |  |  |  |  | 8 | 16647 | 4107
9 | 16392 | 4008 |  | Import Reactive Energy | 0 | 0～9999999.99 | 9 | 16648 | 4108 |  | Import active energy | 0 | 0～9999999.99
10 | 16393 | 4009 |  |  |  |  | 10 | 16649 | 4109
11 | 16394 | 400A |  | Export Reactive Energy | 0 | 0～9999999.99 | 11 | 16650 | 410A |  | Export active energy | 0 | 0～9999999.99
12 | 16395 | 400B |  |  |  |  | 12 | 16651 | 410B
13 | 16396 | 400C | Loop 2 | Total active energy | 0 | 0～9999999.99 | 13 | 16652 | 410C | Loop 3 | Total active energy | 0 | 0～9999999.99
14 | 16397 | 400D |  |  |  |  | 14 | 16653 | 410D
15 | 16398 | 400E |  | Import Active Energy | 0 | 0～9999999.99 | 15 | 16654 | 410E |  | Import active energy | 0 | 0～9999999.99
16 | 16399 | 400F |  |  |  |  | 16 | 16655 | 410F
17 | 16400 | 4010 |  | Export Active Energy | 0 | 0～9999999.99 | 17 | 16656 | 4110 |  | Export active energy | 0 | 0～9999999.99
18 | 16401 | 4011 |  |  |  |  | 18 | 16657 | 4111
19 | 16402 | 4012 |  | Total reactive energy | 0 | 0～9999999.99 | 19 | 16658 | 4112 | Loop 4 | Total active energy | 0 | 0～9999999.99
20 | 16403 | 4013 |  |  |  |  | 20 | 16659 | 4113
21 | 16404 | 4014 |  | Import Reactive Energy | 0 | 0～9999999.99 | 21 | 16660 | 4114 |  | Import active energy | 0 | 0～9999999.99
22 | 16405 | 4015 |  |  |  |  | 22 | 16661 | 4115
23 | 16406 | 4016 |  | Export Reactive Energy | 0 | 0～9999999.99 | 23 | 16662 | 4116 |  | Export active energy | 0 | 0～9999999.99
24 | 16407 | 4017 |  |  |  |  | 24 | 16663 | 4117
25 | 16408 | 4018 | Loop 3 | Total active energy | 0 | 0～9999999.99 | 25 | 16664 | 4118 | Loop 5 | Total active energy | 0 | 0～9999999.99
26 | 16409 | 4019 |  |  |  |  | 26 | 16665 | 4119
27 | 16410 | 401A |  | Import Active Energy | 0 | 0～9999999.99 | 27 | 16666 | 411A |  | Import active energy | 0 | 0～9999999.99
28 | 16411 | 401B |  |  |  |  | 28 | 16667 | 411B
29 | 16412 | 401C |  | Export Active Energy | 0 | 0～9999999.99 | 29 | 16668 | 411C |  | Export active energy | 0 | 0～9999999.99
30 | 16413 | 401D |  |  |  |  | 30 | 16669 | 411D
31 | 16414 | 401E |  | Total reactive energy | 0 | 0～9999999.99 | 31 | 16670 | 411E | Loop 6 | Total active energy | 0 | 0～9999999.99
32 | 16415 | 401F |  |  |  |  | 32 | 16671 | 411F
33 | 16416 | 4020 |  | Import Reactive Energy | 0 | 0～9999999.99 | 33 | 16672 | 4120 |  | Import active energy | 0 | 0～9999999.99
34 | 16417 | 4021 |  |  |  |  | 34 | 16673 | 4121
35 | 16418 | 4022 |  | Export Reactive Energy | 0 | 0～9999999.99 | 35 | 16674 | 4122 |  | Export active energy | 0 | 0～9999999.99
36 | 16419 | 4023 |  |  |  |  | 36 | 16675 | 4123
37 | 16420 | 4024 | Loop 4 | Total active energy | 0 | 0～9999999.99 | 37 | 16676 | 4124 | Loop 7 | Total active energy | 0 | 0～9999999.99
38 | 16421 | 4025 |  |  |  |  | 38 | 16677 | 4125
39 | 16422 | 4026 |  | Import Active Energy | 0 | 0～9999999.99 | 39 | 16678 | 4126 |  | Import active energy | 0 | 0～9999999.99
40 | 16423 | 4027 |  |  |  |  | 40 | 16679 | 4127
41 | 16424 | 4028 |  | Export Active Energy | 0 | 0～9999999.99 | 41 | 16680 | 4128 |  | Export active energy | 0 | 0～9999999.99
42 | 16425 | 4029 |  |  |  |  | 42 | 16681 | 4129
43 | 16426 | 402A |  | Total reactive energy | 0 | 0～9999999.99 | 43 | 16682 | 412A | Loop 8 | Total active energy | 0 | 0～9999999.99
44 | 16427 | 402B |  |  |  |  | 44 | 16683 | 412B
45 | 16428 | 402C |  | Import Reactive Energy | 0 | 0～9999999.99 | 45 | 16684 | 412C |  | Import active energy | 0 | 0～9999999.99
46 | 16429 | 402D |  |  |  |  | 46 | 16685 | 412D
47 | 16430 | 402E |  | Export Reactive Energy | 0 | 0～9999999.99 | 47 | 16686 | 412E |  | Export active energy | 0 | 0～9999999.99
48 | 16431 | 402F |  |  |  |  | 48 | 16687 | 412F
49 | 16432 | 4030 | Loop 5 | Total active energy | 0 | 0～9999999.99 | 49 | 16688 | 4130 | Loop 9 | Total active energy | 0 | 0～9999999.99
50 | 16433 | 4031 |  |  |  |  | 50 | 16689 | 4131
51 | 16434 | 4032 |  | Import Active Energy | 0 | 0～9999999.99 | 51 | 16690 | 4132 |  | Import active energy | 0 | 0～9999999.99
52 | 16435 | 4033 |  |  |  |  | 52 | 16691 | 4133
53 | 16436 | 4034 |  | Export Active Energy | 0 | 0～9999999.99 | 53 | 16692 | 4134 |  | Export active energy | 0 | 0～9999999.99
54 | 16437 | 4035 |  |  |  |  | 54 | 16693 | 4135
55 | 16438 | 4036 |  | Total reactive energy | 0 | 0～9999999.99 | 55 | 16694 | 4136 | Loop 10 | Total active energy | 0 | 0～9999999.99
56 | 16439 | 4037 |  |  |  |  | 56 | 16695 | 4137
57 | 16440 | 4038 |  | Import Reactive Energy | 0 | 0～9999999.99 | 57 | 16696 | 4138 |  | Import active energy | 0 | 0～9999999.99
58 | 16441 | 4039 |  |  |  |  | 58 | 16697 | 4139
59 | 16442 | 403A |  | Export Reactive Energy | 0 | 0～9999999.99 | 59 | 16698 | 413A |  | Export active energy | 0 | 0～9999999.99
60 | 16443 | 403B |  |  |  |  | 60 | 16699 | 413B
61 | 16444 | 403C | Loop 6 | Total active energy | 0 | 0～9999999.99 | 61 | 16700 | 413C | Loop 11 | Total active energy | 0 | 0～9999999.99
62 | 16445 | 403D |  |  |  |  | 62 | 16701 | 413D
63 | 16446 | 403E |  | Import Active Energy | 0 | 0～9999999.99 | 63 | 16702 | 413E |  | Import active energy | 0 | 0～9999999.99
64 | 16447 | 403F |  |  |  |  | 64 | 16703 | 413F
65 | 16448 | 4040 |  | Export Active Energy | 0 | 0～9999999.99 | 65 | 16704 | 4140 |  | Export active energy | 0 | 0～9999999.99
66 | 16449 | 4041 |  |  |  |  | 66 | 16705 | 4141
67 | 16450 | 4042 |  | Total reactive energy | 0 | 0～9999999.99 | 67 | 16706 | 4142 | Loop 12 | Total active energy | 0 | 0～9999999.99
68 | 16451 | 4043 |  |  |  |  | 68 | 16707 | 4143
69 | 16452 | 4044 |  | Import Reactive Energy | 0 | 0～9999999.99 | 69 | 16708 | 4144 |  | Import active energy | 0 | 0～9999999.99
70 | 16453 | 4045 |  |  |  |  | 70 | 16709 | 4145
71 | 16454 | 4046 |  | Export Reactive Energy | 0 | 0～9999999.99 | 71 | 16710 | 4146 |  | Export active energy | 0 | 0～9999999.99
72 | 16455 | 4047 |  |  |  |  | 72 | 16711 | 4147
73 | 16456 | 4048 | Loop 7 | Total active energy | 0 | 0～9999999.99 | 73 | 16712 | 4148 | Loop 13 | Total active energy | 0 | 0～9999999.99
74 | 16457 | 4049 |  |  |  |  | 74 | 16713 | 4149
75 | 16458 | 404A |  | Import Active Energy | 0 | 0～9999999.99 | 75 | 16714 | 414A |  | Import active energy | 0 | 0～9999999.99
76 | 16459 | 404B |  |  |  |  | 76 | 16715 | 414B
77 | 16460 | 404C |  | Export Active Energy | 0 | 0～9999999.99 | 77 | 16716 | 414C |  | Export active energy | 0 | 0～9999999.99
78 | 16461 | 404D |  |  |  |  | 78 | 16717 | 414D
79 | 16462 | 404E |  | Total reactive energy | 0 | 0～9999999.99 | 79 | 16718 | 414E | Loop 14 | Total active energy | 0 | 0～9999999.99
80 | 16463 | 404F |  |  |  |  | 80 | 16719 | 414F
81 | 16464 | 4050 |  | Import Reactive Energy | 0 | 0～9999999.99 | 81 | 16720 | 4150 |  | Import active energy | 0 | 0～9999999.99
82 | 16465 | 4051 |  |  |  |  | 82 | 16721 | 4151
83 | 16466 | 4052 |  | Export Reactive Energy | 0 | 0～9999999.99 | 83 | 16722 | 4152 |  | Export active energy | 0 | 0～9999999.99
84 | 16467 | 4053 |  |  |  |  | 84 | 16723 | 4153
85 | 16468 | 4054 | Loop 8 | Total active energy | 0 | 0～9999999.99 | 85 | 16724 | 4154 | Loop 15 | Total active energy | 0 | 0～9999999.99
86 | 16469 | 4055 |  |  |  |  | 86 | 16725 | 4155
87 | 16470 | 4056 |  | Import Active Energy | 0 | 0～9999999.99 | 87 | 16726 | 4156 |  | Import active energy | 0 | 0～9999999.99
88 | 16471 | 4057 |  |  |  |  | 88 | 16727 | 4157
89 | 16472 | 4058 |  | Export Active Energy | 0 | 0～9999999.99 | 89 | 16728 | 4158 |  | Export active energy | 0 | 0～9999999.99
90 | 16473 | 4059 |  |  |  |  | 90 | 16729 | 4159
91 | 16474 | 405A |  | Total reactive energy | 0 | 0～9999999.99 | 91 | 16730 | 415A | Loop 16 | Total active energy | 0 | 0～9999999.99
92 | 16475 | 405B |  |  |  |  | 92 | 16731 | 415B
93 | 16476 | 405C |  | Import Reactive Energy | 0 | 0～9999999.99 | 93 | 16732 | 415C |  | Import active energy | 0 | 0～9999999.99
94 | 16477 | 405D |  |  |  |  | 94 | 16733 | 415D
95 | 16478 | 405E |  | Export Reactive Energy | 0 | 0～9999999.99 | 95 | 16734 | 415E |  | Export active energy | 0 | 0～9999999.99
96 | 16479 | 405F |  |  |  |  | 96 | 16735 | 415F
97 | 16480 | 4060 | Loop 9 | Total active energy | 0 | 0～9999999.99 | 97 | 16736 | 4160 | Loop 17 | Total active energy | 0 | 0～9999999.99
98 | 16481 | 4061 |  |  |  |  | 98 | 16737 | 4161
99 | 16482 | 4062 |  | Import Active Energy | 0 | 0～9999999.99 | 99 | 16738 | 4162 |  | Import active energy | 0 | 0～9999999.99
100 | 16483 | 4063 |  |  |  |  | 100 | 16739 | 4163
101 | 16484 | 4064 |  | Export Active Energy | 0 | 0～9999999.99 | 101 | 16740 | 4164 |  | Export active energy | 0 | 0～9999999.99
102 | 16485 | 4065 |  |  |  |  | 102 | 16741 | 4165
103 | 16486 | 4066 |  | Total reactive energy | 0 | 0～9999999.99 | 103 | 16742 | 4166 | Loop 18 | Total active energy | 0 | 0～9999999.99
104 | 16487 | 4067 |  |  |  |  | 104 | 16743 | 4167
105 | 16488 | 4068 |  | Import Reactive Energy | 0 | 0～9999999.99 | 105 | 16744 | 4168 |  | Import active energy | 0 | 0～9999999.99
106 | 16489 | 4069 |  |  |  |  | 106 | 16745 | 4169
107 | 16490 | 406A |  | Export Reactive Energy | 0 | 0～9999999.99 | 107 | 16746 | 416A |  | Export active energy | 0 | 0～9999999.99
108 | 16491 | 406B |  |  |  |  | 108 | 16747 | 416B
[7 empty] | 109 | 16748 | 416C | Loop 19 | Total active energy | 0 | 0～9999999.99
[7 empty] | 110 | 16749 | 416D
[7 empty] | 111 | 16750 | 416E |  | Import active energy | 0 | 0～9999999.99
[7 empty] | 112 | 16751 | 416F
[7 empty] | 113 | 16752 | 4170 |  | Export active energy | 0 | 0～9999999.99
[7 empty] | 114 | 16753 | 4171
[7 empty] | 115 | 16754 | 4172 | Loop 20 | Total active energy | 0 | 0～9999999.99
[7 empty] | 116 | 16755 | 4173
[7 empty] | 117 | 16756 | 4174 |  | Import active energy | 0 | 0～9999999.99
[7 empty] | 118 | 16757 | 4175
[7 empty] | 119 | 16758 | 4176 |  | Export active energy | 0 | 0～9999999.99
[7 empty] | 120 | 16759 | 4177
[7 empty] | 121 | 16760 | 4178 | Loop 21 | Total active energy | 0 | 0～9999999.99
[7 empty] | 122 | 16761 | 4179
[7 empty] | 123 | 16762 | 417A |  | Import active energy | 0 | 0～9999999.99
[7 empty] | 124 | 16763 | 417B
[7 empty] | 125 | 16764 | 417C |  | Export active energy | 0 | 0～9999999.99
[7 empty] | 126 | 16765 | 417D
[7 empty] | 127 | 16766 | 417E | Loop 22 | Total active energy | 0 | 0～9999999.99
[7 empty] | 128 | 16767 | 417F
[7 empty] | 129 | 16768 | 4180 |  | Import active energy | 0 | 0～9999999.99
[7 empty] | 130 | 16769 | 4181
[7 empty] | 131 | 16770 | 4182 |  | Export active energy | 0 | 0～9999999.99
[7 empty] | 132 | 16771 | 4183
[7 empty] | 133 | 16772 | 4184 | Loop 23 | Total active energy | 0 | 0～9999999.99
[7 empty] | 134 | 16773 | 4185
[7 empty] | 135 | 16774 | 4186 |  | Import active energy | 0 | 0～9999999.99
[7 empty] | 136 | 16775 | 4187
[7 empty] | 137 | 16776 | 4188 |  | Export active energy | 0 | 0～9999999.99
[7 empty] | 138 | 16777 | 4189
[7 empty] | 139 | 16778 | 418A | Loop 24 | Total active energy | 0 | 0～9999999.99
[7 empty] | 140 | 16779 | 418B
[7 empty] | 141 | 16780 | 418C |  | Import active energy | 0 | 0～9999999.99
[7 empty] | 142 | 16781 | 418D
[7 empty] | 143 | 16782 | 418E |  | Export active energy | 0 | 0～9999999.99
[7 empty] | 144 | 16783 | 418F
[7 empty] | 145 | 16784 | 4190 | Loop 25 | Total active energy | 0 | 0～9999999.99
[7 empty] | 146 | 16785 | 4191
[7 empty] | 147 | 16786 | 4192 |  | Import active energy | 0 | 0～9999999.99
[7 empty] | 148 | 16787 | 4193
[7 empty] | 149 | 16788 | 4194 |  | Export active energy | 0 | 0～9999999.99
[7 empty] | 150 | 16789 | 4195
[7 empty] | 151 | 16790 | 4196 | Loop 26 | Total active energy | 0 | 0～9999999.99
[7 empty] | 152 | 16791 | 4197
[7 empty] | 153 | 16792 | 4198 |  | Import active energy | 0 | 0～9999999.99
[7 empty] | 154 | 16793 | 4199
[7 empty] | 155 | 16794 | 419A |  | Export active energy | 0 | 0～9999999.99
[7 empty] | 156 | 16795 | 419B
[7 empty] | 157 | 16796 | 419C | Loop 27 | Total active energy | 0 | 0～9999999.99
[7 empty] | 158 | 16797 | 419D
[7 empty] | 159 | 16798 | 419E |  | Import active energy | 0 | 0～9999999.99
[7 empty] | 160 | 16799 | 419F
[7 empty] | 161 | 16800 | 41A0 |  | Export active energy | 0 | 0～9999999.99
[7 empty] | 162 | 16801 | 41A1

## Basic Set
Basic Set Parameters Zone
Add (Decimal) | Address (Hexadecimal) | Parameter | Type | Default Value | Value Range
8192 | 2000 | Password protection (basic parameter protection) | Read/Write | 0 | 0～9999
8193 | 2001 | Communication address | Read/Write | 1 | 1～247
8194 | 2002 | RS485-1 serial port parameter （high byte is parity check,low byte is baud rate） | Read/Write | 0,3 | High：0:(N,8,1)，1:(E,8,1)，2:(O,8,1) Low：0:9600, 1:2400, 2:4800, 3:9600，4:19200
8195 | 2003 | RS485-2 serial port parameter （high byte is parity check,low byte is baud rate） | Read/Write | 0,3 | High：0:(N,8,1)，1:(E,8,1)，2:(O,8,1) Low：0:9600, 1:2400, 2:4800, 3:9600，4:19200
8196 | 2004 | Voltage connection mode | Read/Write | 0 | 0：3LN，1：2LL
8197 | 2005 | PT | Read/Write | 1 | 1∼9999 (remark 1)
8198 | 2006 | CT1 A | Read/Write | 1 | 1∼9999 (remark 1)
8199 | 2007 | CT1 B | Read/Write | 1 | 1∼9999 (remark 1)
8200 | 2008 | CT1 C | Read/Write | 1 | 1∼9999 (remark 1)
8201 | 2009 | CT2 A | Read/Write | 1 | 1∼9999 (remark 1)
8202 | 200a | CT2 B | Read/Write | 1 | 1∼9999 (remark 1)
8203 | 200b | CT2 C | Read/Write | 1 | 1∼9999 (remark 1)
8204 | 200c | CT3 A | Read/Write | 1 | 1∼9999 (remark 1)
8205 | 200d | CT3 B | Read/Write | 1 | 1∼9999 (remark 1)
8206 | 200e | CT3 C | Read/Write | 1 | 1∼9999 (remark 1)
8207 | 200f | CT4 A | Read/Write | 1 | 1∼9999 (remark 1)
8208 | 2010 | CT4 B | Read/Write | 1 | 1∼9999 (remark 1)
8209 | 2011 | CT4 C | Read/Write | 1 | 1∼9999 (remark 1)
8210 | 2012 | CT5 A | Read/Write | 1 | 1∼9999 (remark 1)
8211 | 2013 | CT5 B | Read/Write | 1 | 1∼9999 (remark 1)
8212 | 2014 | CT5 C | Read/Write | 1 | 1∼9999 (remark 1)
8213 | 2015 | CT6 A | Read/Write | 1 | 1∼9999 (remark 1)
8214 | 2016 | CT6 B | Read/Write | 1 | 1∼9999 (remark 1)
8215 | 2017 | CT6 C | Read/Write | 1 | 1∼9999 (remark 1)
8216 | 2018 | CT7 A | Read/Write | 1 | 1∼9999 (remark 1)
8217 | 2019 | CT7 B | Read/Write | 1 | 1∼9999 (remark 1)
8218 | 201a | CT7 C | Read/Write | 1 | 1∼9999 (remark 1)
8219 | 201b | CT8 A | Read/Write | 1 | 1∼9999 (remark 1)
8220 | 201c | CT8 B | Read/Write | 1 | 1∼9999 (remark 1)
8221 | 201d | CT8 C | Read/Write | 1 | 1∼9999 (remark 1)
8222 | 201e | CT9 A | Read/Write | 1 | 1∼9999 (remark 1)
8223 | 201f | CT9 B | Read/Write | 1 | 1∼9999 (remark 1)
8224 | 2020 | CT9 C | Read/Write | 1 | 1∼9999 (remark 1)
8225 | 2021 | CF1 output type | Read/Write |  | high bytes of which loop; low byte type(remark 2)
8226 | 2022 | CF2 output type | Read/Write |  | high bytes of which loop; low byte type(remark 2)
8227 | 2023 | Electric energy pulse constant | Read/Write | 9600 | 600～50000
remark 1: product of CT and PT should be less than 300,000.
remark 2: high bytes:0-8;low bytes:0-5.Meanings of low bytes: 0 is full-wave active energy; 1 is full-wave reactive energy; 2 is full-wave apparent power; 3 is fundamental active energy; 4 is fundamental reactive energy; 5 is fundamental apparent power.
Command
| Clear Energy | 01 10 cd10 0002 04 5555 6666
| Address | Description | Data
| CD10 | Clear Energy Value | 5555 6666