## 0XXX Zone DIDO
DI Zone
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Register Type | Type | Name | Data Type | Default | Value Range | Remark
1 | 0 | 0000 | 02 | Read | DI | DI1 | bit | 0 | 0-1 | 0:Open 1:Close
2 | 1 | 0001 | 02 | Read |  | DI2 | bit | 0 | 0-1
DO Status
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Register Type | Type | Name | Data Type | Default | Value Range | Remark
1 | 2048 | 0800 | 01/05 | Read/Write | DO | DO1 | bit | 0 | Write：FF00/0000 Read：0～0x0F | Write：0000-Open FF00-Close Read：0-Open 1-Close
2 | 2049 | 0801 | 01/05 | Read/Write |  | DO2 | bit | 0 | Write：FF00/0000 Read：0～0x0F

## 1XXX Zone 1.25mA (hidden)
Basic Parameters (Secondary Current 1.25mA)
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range |  | Remarks
1 | 4096 | 1000 | 04 | Read | phase voltage | phase A voltage | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
2 | 4097 | 1001 | 04 | Read |  | phase B voltage | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
3 | 4098 | 1002 | 04 | Read |  | phase C voltage | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
4 | 4099 | 1003 | 04 | Read |  | phase voltage mean value | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
5 | 4100 | 1004 | 04 | Read |  | zero sequence voltage | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
6 | 4101 | 1005 | 04 | Read | line voltage | line voltage(A-B) | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
7 | 4102 | 1006 | 04 | Read |  | line voltage(B-C) | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
8 | 4103 | 1007 | 04 | Read |  | line voltage(C-A) | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
9 | 4104 | 1008 | 04 | Read |  | line voltage mean value | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
10 | 4105 | 1009 | 04 | Read | current | phase A current | unsigned 16 bit | 0 | 0～65535 | A | amplify 1000 times
11 | 4106 | 100A | 04 | Read |  | phase B current | unsigned 16 bit | 0 | 0～65535 | A | amplify 1000 times
12 | 4107 | 100B | 04 | Read |  | phase C current | unsigned 16 bit | 0 | 0～65535 | A | amplify 1000 times
13 | 4108 | 100C | 04 | Read |  | average current | unsigned 16 bit | 0 | 0～65535 | A | amplify 1000 times
14 | 4109 | 100D | 04 | Read |  | zero-sequence current IN | unsigned 16 bit | 0 | 0～65535 | A | amplify 1000 times
15 | 4110 | 100E | 04 | Read | active power | A phase active power | signed 16 bit | 0 | -32768～32767 | kW | amplify 1000 times
16 | 4111 | 100F | 04 | Read |  | B phase active power | signed 16 bit | 0 | -32768～32767 | kW | amplify 1000 times
17 | 4112 | 1010 | 04 | Read |  | C phase active power | signed 16 bit | 0 | -32768～32767 | kW | amplify 1000 times
18 | 4113 | 1011 | 04 | Read |  | Total active power | signed 16 bit | 0 | -32768～32767 | kW | amplify 1000 times
19 | 4114 | 1012 | 04 | Read | reactive power | A phase reactive power | signed 16 bit | 0 | -32768～32767 | kvar | amplify 1000 times
20 | 4115 | 1013 | 04 | Read |  | B phase reactive power | signed 16 bit | 0 | -32768～32767 | kvar | amplify 1000 times
21 | 4116 | 1014 | 04 | Read |  | C phase reactive power | signed 16 bit | 0 | -32768～32767 | kvar | amplify 1000 times
22 | 4117 | 1015 | 04 | Read |  | Total reactive power | signed 16 bit | 0 | -32768～32767 | kvar | amplify 1000 times
23 | 4118 | 1016 | 04 | Read | apparent power | A phase apparent power | unsigned 16 bit | 0 | 0～65535 | kVA | amplify 1000 times
24 | 4119 | 1017 | 04 | Read |  | B phase apparent power | unsigned 16 bit | 0 | 0～65535 | kVA | amplify 1000 times
25 | 4120 | 1018 | 04 | Read |  | C phase apparent power | unsigned 16 bit | 0 | 0～65535 | kVA | amplify 1000 times
26 | 4121 | 1019 | 04 | Read |  | Total apparent power | unsigned 16 bit | 0 | 0～65535 | kVA | amplify 1000 times
27 | 4122 | 101A | 04 | Read | power factor | A phase power factor | signed 16 bit | 0 | -1000～1000 | —— | amplify 1000 times
28 | 4123 | 101B | 04 | Read |  | B phase power factor | signed 16 bit | 0 | -1000～1000 | —— | amplify 1000 times
29 | 4124 | 101C | 04 | Read |  | C phase power factor | signed 16 bit | 0 | -1000～1000 | —— | amplify 1000 times
30 | 4125 | 101D | 04 | Read |  | power factor | signed 16 bit | 0 | -1000～1000 | —— | amplify 1000 times
31 | 4126 | 101E | 04 | Read | frequency | frequency | unsigned 16 bit | 0 | 0～65535 | Hz | amplify 100 times
32 | 4127 | 101F | 04 | Read | imbalance | voltage imbalance | unsigned 16 bit | 0 | 0～65535 | —— | amplify 100 times
33 | 4128 | 1020 | 04 | Read |  | current imbalance | unsigned 16 bit | 0 | 0～65535 | —— | amplify 100 times
34 | 4129 | 1021 | 04 | Read | temperature | T1 temperature | signed 16 bit | 0 | -32768～32767 | ℃ | amplify 10 times
35 | 4130 | 1022 | 04 | Read |  | T2 temperature | signed 16 bit | 0 | -32768～32767 | ℃ | amplify 10 times
36 | 4131 | 1023 | 04 | Read |  | T3 temperature | signed 16 bit | 0 | -32768～32767 | ℃ | amplify 10 times
37 | 4132 | 1024 | 04 | Read |  | T4 temperature | signed 16 bit | 0 | -32768～32767 | ℃ | amplify 10 times
38 | 4133 | 1025 | 04 | Read | leakage current | full wave leakage current | unsigned 16 bit | 0 | 0～65535 | A | amplify 1000 times
39 | 4134 | 1026 | 04 | Read |  | fundamental leakage current | unsigned 16 bit | 0 | 0～65535 | A | amplify 1000 times
40 | 4135 | 1027 | 04 | Read | demand | high | unsigned 32 bit | 0 | 0～65535 | kW | amplify 1000 times
41 | 4136 | 1028 | 04 | Read |  | low
42 | 4137 | 1029 | 04 | Read | phase angle | U-U ab | unsigned 16 bit | 0 | 0～359 | 1°
43 | 4138 | 102A | 04 | Read |  | U-U bc | unsigned 16 bit | 0 | 0～359 | 1°
44 | 4139 | 102B | 04 | Read |  | U-U ca | unsigned 16 bit | 0 | 0～359 | 1°
45 | 4140 | 102C | 04 | Read |  | U-I ab | unsigned 16 bit | 0 | 0～359 | 1°
46 | 4141 | 102D | 04 | Read |  | U-I bc | unsigned 16 bit | 0 | 0～359 | 1°
47 | 4142 | 102E | 04 | Read |  | U-I ca | unsigned 16 bit | 0 | 0～359 | 1°
48 | 4143 | 102F | 04 | Read |  | I-I ab | unsigned 16 bit | 0 | 0～359 | 1°
49 | 4144 | 1030 | 04 | Read |  | I-I bc | unsigned 16 bit | 0 | 0～359 | 1°
50 | 4145 | 1031 | 04 | Read |  | I-I ca | unsigned 16 bit | 0 | 0～359 | 1°
51 | 4146 | 1032 | 04 | Read |  | normal phase angle sign | unsigned 16 bit | 0 | 0～1 | —— | 0: abnormal 1：normal
52 | 4147 | 1033 | 04 | Read | signal strength | wireless signal strength | unsigned 16 bit | 0 | 0～99 | ——
53 | 4148 | 1034 | 04 | Read | hardware version | high 2 bit | ASCII | 0X312E | 0～65535 | —— | ASCII format represent default is 1.0.0
54 | 4149 | 1035 | 04 | Read |  | middle 2 bit | ASCII | 0X302E
55 | 4150 | 1036 | 04 | Read |  | low 2 bit（reserved） | ASCII | 0X3000
56 | 4151 | 1037 | 04 | Read | software version | high 2 bit | ASCII | 0X312E | 0～65535 | —— | ASCII format represent default is 1.0.0
57 | 4152 | 1038 | 04 | Read |  | middle 2 bit | ASCII | 0X302E
58 | 4153 | 1039 | 04 | Read |  | low 1 bit（reserved） | ASCII | 0X3000
59 | 4154 | 103A | 04 | Read | DI | DI1 | unsigned 16 bit | 0 | 0～1 | —— | 0: open 1: close
60 | 4155 | 103B | 04 | Read |  | DI2 | unsigned 16 bit | 0 | 0～1 | ——
61 | 4156 | 103C | 04 | Read | internet status | wireless internet status | unsigned 16 bit |  | 0~64 | ——
62 | 4157 | 103D | 04 | Read | voltage imbalance | phase A voltage imbalance | signed 16 bit |  |  | ——
63 | 4158 | 103E | 04 | Read |  | phase B voltage imbalance | signed 16 bit |  |  | ——
64 | 4159 | 103F | 04 | Read |  | phase C voltage imbalance | signed 16 bit |  |  | ——
65 | 4160 | 1040 | 04 | Read |  | average voltage imbalance | signed 16 bit |  |  | ——
66 | 4161 | 1041 | 04 | Read | current month volatge qualification rate |  | unsigned 16 bit |  |  | ——
67 | 4162 | 1042 | 04 | Read | last month volatge qualification rate |  | unsigned 16 bit |  |  | ——
Wireless signal strength instruction：0 –≤ -113；1 – -111 dBm；2~30 – -109~-53 dBm；31 –≥ -51 dBm；99 – unknown；

## 1XXX Zone 100mA
Basic Parameters (Secondary Current 100mA)
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range |  | Remarks
1 | 4096 | 1000 | 04 | Read | phase voltage | phase A voltage | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
2 | 4097 | 1001 | 04 | Read |  | phase B voltage | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
3 | 4098 | 1002 | 04 | Read |  | phase C voltage | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
4 | 4099 | 1003 | 04 | Read |  | phase voltage mean value | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
5 | 4100 | 1004 | 04 | Read |  | zero sequence voltage | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
6 | 4101 | 1005 | 04 | Read | line voltage | line voltage(A-B) | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
7 | 4102 | 1006 | 04 | Read |  | line voltage(B-C) | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
8 | 4103 | 1007 | 04 | Read |  | line voltage(C-A) | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
9 | 4104 | 1008 | 04 | Read |  | line voltage mean value | unsigned 16 bit | 0 | 0～65535 | V | amplify 100 times
10 | 4105 | 1009 | 04 | Read | current | phase A current | unsigned 16 bit | 0 | 0～65535 | mA | amplify 100 times
11 | 4106 | 100A | 04 | Read |  | phase B current | unsigned 16 bit | 0 | 0～65535 | mA | amplify 100 times
12 | 4107 | 100B | 04 | Read |  | phase C current | unsigned 16 bit | 0 | 0～65535 | mA | amplify 100 times
13 | 4108 | 100C | 04 | Read |  | average current | unsigned 16 bit | 0 | 0～65535 | mA | amplify 100 times
14 | 4109 | 100D | 04 | Read |  | zero-sequence current IN | unsigned 16 bit | 0 | 0～65535 | mA | amplify 100 times
15 | 4110 | 100E | 04 | Read | active power | A phase active power | signed 16 bit | 0 | -32768～32767 | W | amplify 100 times
16 | 4111 | 100F | 04 | Read |  | B phase active power | signed 16 bit | 0 | -32768～32767 | W | amplify 100 times
17 | 4112 | 1010 | 04 | Read |  | C phase active power | signed 16 bit | 0 | -32768～32767 | W | amplify 100 times
18 | 4113 | 1011 | 04 | Read |  | Total active power | signed 16 bit | 0 | -32768～32767 | W | amplify 100 times
19 | 4114 | 1012 | 04 | Read | reactive power | A phase reactive power | signed 16 bit | 0 | -32768～32767 | var | amplify 100 times
20 | 4115 | 1013 | 04 | Read |  | B phase reactive power | signed 16 bit | 0 | -32768～32767 | var | amplify 100 times
21 | 4116 | 1014 | 04 | Read |  | C phase reactive power | signed 16 bit | 0 | -32768～32767 | var | amplify 100 times
22 | 4117 | 1015 | 04 | Read |  | Total reactive power | signed 16 bit | 0 | -32768～32767 | var | amplify 100 times
23 | 4118 | 1016 | 04 | Read | apparent power | A phase apparent power | unsigned 16 bit | 0 | 0～65535 | VA | amplify 100 times
24 | 4119 | 1017 | 04 | Read |  | B phase apparent power | unsigned 16 bit | 0 | 0～65535 | VA | amplify 100 times
25 | 4120 | 1018 | 04 | Read |  | C phase apparent power | unsigned 16 bit | 0 | 0～65535 | VA | amplify 100 times
26 | 4121 | 1019 | 04 | Read |  | Total apparent power | unsigned 16 bit | 0 | 0～65535 | VA | amplify 100 times
27 | 4122 | 101A | 04 | Read | power factor | A phase power factor | signed 16 bit | 0 | -100～100 | —— | amplify 100 times
28 | 4123 | 101B | 04 | Read |  | B phase power factor | signed 16 bit | 0 | -100～100 | —— | amplify 100 times
29 | 4124 | 101C | 04 | Read |  | C phase power factor | signed 16 bit | 0 | -100～100 | —— | amplify 100 times
30 | 4125 | 101D | 04 | Read |  | power factor | signed 16 bit | 0 | -100～100 | —— | amplify 100 times
31 | 4126 | 101E | 04 | Read | frequency | frequency | unsigned 16 bit | 0 | 0～65535 | Hz | amplify 100 times
32 | 4127 | 101F | 04 | Read | imbalance | voltage imbalance | unsigned 16 bit | 0 | 0～65535 | —— | amplify 100 times
33 | 4128 | 1020 | 04 | Read |  | current imbalance | unsigned 16 bit | 0 | 0～65535 | —— | amplify 100 times
34 | 4129 | 1021 | 04 | Read | temperature | T1 temperature | signed 16 bit | 0 | -32768～32767 | ℃ | amplify 10 times
35 | 4130 | 1022 | 04 | Read |  | T2 temperature | signed 16 bit | 0 | -32768～32767 | ℃ | amplify 10 times
36 | 4131 | 1023 | 04 | Read |  | T3 temperature | signed 16 bit | 0 | -32768～32767 | ℃ | amplify 10 times
37 | 4132 | 1024 | 04 | Read |  | T4 temperature | signed 16 bit | 0 | -32768～32767 | ℃ | amplify 10 times
38 | 4133 | 1025 | 04 | Read | leakage current | full wave leakage current | unsigned 16 bit | 0 | 0～65535 | A | amplify 1000 times
39 | 4134 | 1026 | 04 | Read |  | fundamental leakage current | unsigned 16 bit | 0 | 0～65535 | A | amplify 1000 times
40 | 4135 | 1027 | 04 | Read | demand | high | unsigned 32 bit | 0 | 0～65535 | W | amplify 100 times
41 | 4136 | 1028 | 04 | Read |  | low
42 | 4137 | 1029 | 04 | Read | phase angle | U-U ab | unsigned 16 bit | 0 | 0～359 | 1°
43 | 4138 | 102A | 04 | Read |  | U-U bc | unsigned 16 bit | 0 | 0～359 | 1°
44 | 4139 | 102B | 04 | Read |  | U-U ca | unsigned 16 bit | 0 | 0～359 | 1°
45 | 4140 | 102C | 04 | Read |  | U-I ab | unsigned 16 bit | 0 | 0～359 | 1°
46 | 4141 | 102D | 04 | Read |  | U-I bc | unsigned 16 bit | 0 | 0～359 | 1°
47 | 4142 | 102E | 04 | Read |  | U-I ca | unsigned 16 bit | 0 | 0～359 | 1°
48 | 4143 | 102F | 04 | Read |  | I-I ab | unsigned 16 bit | 0 | 0～359 | 1°
49 | 4144 | 1030 | 04 | Read |  | I-I bc | unsigned 16 bit | 0 | 0～359 | 1°
50 | 4145 | 1031 | 04 | Read |  | I-I ca | unsigned 16 bit | 0 | 0～359 | 1°
51 | 4146 | 1032 | 04 | Read |  | normal phase angle sign | unsigned 16 bit | 0 | 0: abnormal 1：normal | —— | 0: abnormal 1：normal
52 | 4147 | 1033 | 04 | Read | signal strength | wireless signal strength | unsigned 16 bit | 0 | 0～99 | ——
53 | 4148 | 1034 | 04 | Read | hardware version | high 2 bit | ASCII | 0X312E | 0～65535 | —— | ASCII format represent default is 1.0.0
54 | 4149 | 1035 | 04 | Read |  | middle 2 bit | ASCII | 0X302E
55 | 4150 | 1036 | 04 | Read |  | low 1 bit（reserved） | ASCII | 0X3000
56 | 4151 | 1037 | 04 | Read | software version | high 2 bit | ASCII | 0X312E | 0～65535 | —— | ASCII format represent default is 1.0.0
57 | 4152 | 1038 | 04 | Read |  | middle 2 bit | ASCII | 0X302E
58 | 4153 | 1039 | 04 | Read |  | low 1 bit（reserved） | ASCII | 0X3000
59 | 4154 | 103A | 04 | Read | DI | DI1 | unsigned 16 bit | 0 | 0～1 | —— | 0: open 1: close
60 | 4155 | 103B | 04 | Read |  | DI2 | unsigned 16 bit | 0 | 0～1 | ——
61 | 4156 | 103C | 04 | Read | internet status | wireless internet status | unsigned 16 bit |  | 0~64 | ——
62 | 4157 | 103D | 04 | Read | voltage imbalance | phase A voltage imbalance | signed 16 bit |  |  | ——
63 | 4158 | 103E | 04 | Read |  | phase B voltage imbalance | signed 16 bit |  |  | ——
64 | 4159 | 103F | 04 | Read |  | phase C voltage imbalance | signed 16 bit |  |  | ——
65 | 4160 | 1040 | 04 | Read |  | average voltage imbalance | signed 16 bit |  |  | ——
66 | 4161 | 1041 | 04 | Read | current month volatge qualification rate |  | unsigned 16 bit |  |  | ——
67 | 4162 | 1042 | 04 | Read | last month volatge qualification rate |  | unsigned 16 bit |  |  | ——
Wireless signal strength instruction：0 –≤ -113；1 – -111 dBm；2~30 – -109~-53 dBm；31 –≥ -51 dBm；99 – unknown；

## 1XXX Zone Primary Current
Basically Measured Parameters Zone（primary measurement）
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range |  | Remarks
1 | 5376 | 1500 | 04 | Read | phase voltage | phase A voltage | unsigned 32 bit | 0 | 0～4294967295 | V | amplify 100 times
2 | 5377 | 1501 | 04 | Read
3 | 5378 | 1502 | 04 | Read |  | phase B voltage | unsigned 32 bit | 0 | 0～4294967295 | V | amplify 100 times
4 | 5379 | 1503 | 04 | Read
5 | 5380 | 1504 | 04 | Read |  | phase C voltage | unsigned 32 bit | 0 | 0～4294967295 | V | amplify 100 times
6 | 5381 | 1505 | 04 | Read
7 | 5382 | 1506 | 04 | Read |  | phase voltage mean value | unsigned 32 bit | 0 | 0～4294967295 | V | amplify 100 times
8 | 5383 | 1507 | 04 | Read
9 | 5384 | 1508 | 04 | Read |  | zero sequence voltage | unsigned 32 bit | 0 | 0～4294967295 | V | amplify 100 times
10 | 5385 | 1509 | 04 | Read
11 | 5386 | 150A | 04 | Read | line voltage | line voltage(A-B) | unsigned 32 bit | 0 | 0～4294967295 | V | amplify 100 times
12 | 5387 | 150B | 04 | Read
13 | 5388 | 150C | 04 | Read |  | line voltage(B-C) | unsigned 32 bit | 0 | 0～4294967295 | V | amplify 100 times
14 | 5389 | 150D | 04 | Read
15 | 5390 | 150E | 04 | Read |  | line voltage(C-A) | unsigned 32 bit | 0 | 0～4294967295 | V | amplify 100 times
16 | 5391 | 150F | 04 | Read
17 | 5392 | 1510 | 04 | Read |  | line voltage mean value | unsigned 32 bit | 0 | 0～4294967295 | V | amplify 100 times
18 | 5393 | 1511 | 04 | Read
19 | 5394 | 1512 | 04 | Read | current | phase A current | unsigned 32 bit | 0 | 0～4294967295 | A | amplify 1000 times
20 | 5395 | 1513 | 04 | Read
21 | 5396 | 1514 | 04 | Read |  | phase B current | unsigned 32 bit | 0 | 0～4294967295 | A | amplify 1000 times
22 | 5397 | 1515 | 04 | Read
23 | 5398 | 1516 | 04 | Read |  | phase C current | unsigned 32 bit | 0 | 0～4294967295 | A | amplify 1000 times
24 | 5399 | 1517 | 04 | Read
25 | 5400 | 1518 | 04 | Read |  | average current | unsigned 32 bit | 0 | 0～4294967295 | A | amplify 1000 times
26 | 5401 | 1519 | 04 | Read
27 | 5402 | 151A | 04 | Read |  | zero-sequence current | unsigned 32 bit | 0 | 0～4294967295 | A | amplify 1000 times
28 | 5403 | 151B | 04 | Read
29 | 5404 | 151C | 04 | Read | active power | A phase active power | signed 32 bit | 0 | -2147483647～2147483647 | kW | amplify 1000 times
30 | 5405 | 151D | 04 | Read
31 | 5406 | 151E | 04 | Read |  | B phase active power | signed 32 bit | 0 | -2147483647～2147483647 | kW | amplify 1000 times
32 | 5407 | 151F | 04 | Read
33 | 5408 | 1520 | 04 | Read |  | C phase active power | signed 32 bit | 0 | -2147483647～2147483647 | kW | amplify 1000 times
34 | 5409 | 1521 | 04 | Read
35 | 5410 | 1522 | 04 | Read |  | Total active power | signed 32 bit | 0 | -2147483647～2147483647 | kW | amplify 1000 times
36 | 5411 | 1523 | 04 | Read
37 | 5412 | 1524 | 04 | Read | reactive power | A phase reactive power | signed 32 bit | 0 | -2147483647～2147483647 | kvar | amplify 1000 times
38 | 5413 | 1525 | 04 | Read
39 | 5414 | 1526 | 04 | Read |  | B phase reactive power | signed 32 bit | 0 | -2147483647～2147483647 | kvar | amplify 1000 times
40 | 5415 | 1527 | 04 | Read
41 | 5416 | 1528 | 04 | Read |  | C phase reactive power | signed 32 bit | 0 | -2147483647～2147483647 | kvar | amplify 1000 times
42 | 5417 | 1529 | 04 | Read
43 | 5418 | 152A | 04 | Read |  | Total reactive power | signed 32 bit | 0 | -2147483647～2147483647 | kvar | amplify 1000 times
44 | 5419 | 152B | 04 | Read
45 | 5420 | 152C | 04 | Read | apparent power | A phase apparent power | unsigned 32 bit | 0 | 0～4294967295 | kVA | amplify 1000 times
46 | 5421 | 152D | 04 | Read
47 | 5422 | 152E | 04 | Read |  | B phase apparent power | unsigned 32 bit | 0 | 0～4294967295 | kVA | amplify 1000 times
48 | 5423 | 152F | 04 | Read
49 | 5424 | 1530 | 04 | Read |  | C phase apparent power | unsigned 32 bit | 0 | 0～4294967295 | kVA | amplify 1000 times
50 | 5425 | 1531 | 04 | Read
51 | 5426 | 1532 | 04 | Read |  | Total apparent power | unsigned 32 bit | 0 | 0～4294967295 | kVA | amplify 1000 times
52 | 5427 | 1533 | 04 | Read
53 | 5428 | 1534 | 04 | Read | power factor | A phase power factor | signed 16 bit | 0 | -1000～1000 | —— | amplify 1000 times
54 | 5429 | 1535 | 04 | Read |  | B phase power factor | signed 16 bit | 0 | -1000～1000 | —— | amplify 1000 times
55 | 5430 | 1536 | 04 | Read |  | C phase power factor | signed 16 bit | 0 | -1000～1000 | —— | amplify 1000 times
56 | 5431 | 1537 | 04 | Read |  | power factor | signed 16 bit | 0 | -1000～1000 | —— | amplify 1000 times
57 | 5432 | 1538 | 04 | Read | frequency | frequency | unsigned 16 bit | 0 | 0～65535 | Hz | amplify 100 times
58 | 5433 | 1539 | 04 | Read | imbalance | voltage imbalance | unsigned 16 bit | 0 | 0～65535 | —— | amplify 100 times
59 | 5434 | 153A | 04 | Read |  | current imbalance | unsigned 16 bit | 0 | 0～65535 | —— | amplify 100 times
60 | 5435 | 153B | 04 | Read | temperature | T1 temperature | signed 16 bit | 0 | -32768～32767 | ℃ | amplify 10 times
61 | 5436 | 153C | 04 | Read |  | T2 temperature | signed 16 bit | 0 | -32768～32767 | ℃ | amplify 10 times
62 | 5437 | 153D | 04 | Read |  | T3 temperature | signed 16 bit | 0 | -32768～32767 | ℃ | amplify 10 times
63 | 5438 | 153E | 04 | Read |  | T4 temperature | signed 16 bit | 0 | -32768～32767 | ℃ | amplify 10 times
64 | 5439 | 153F | 04 | Read | leakage current | full wave leakage current | unsigned 32 bit | 0 | 0～4294967295 | A | amplify 10000 times
65 | 5440 | 1540 | 04 | Read
66 | 5441 | 1541 | 04 | Read |  | fundamental leakage current | unsigned 32 bit | 0 | 0～4294967295 | A | amplify 10000 times
67 | 5442 | 1542 | 04 | Read
68 | 5443 | 1543 | 04 | Read | demand | high | unsigned 32 bit | 0 | 0～4294967295 | kW | amplify 1000 times
69 | 5444 | 1544 | 04 | Read |  | low
70 | 5445 | 1545 | 04 | Read | phase angle | U-U ab | unsigned 16 bit |  | 0～359 | 1°
71 | 5446 | 1546 | 04 | Read |  | U-U bc | unsigned 16 bit |  | 0～359 | 1°
72 | 5447 | 1547 | 04 | Read |  | U-U ca | unsigned 16 bit |  | 0～359 | 1°
73 | 5448 | 1548 | 04 | Read |  | U-I ab | unsigned 16 bit |  | 0～359 | 1°
74 | 5449 | 1549 | 04 | Read |  | U-I bc | unsigned 16 bit |  | 0～359 | 1°
75 | 5450 | 154A | 04 | Read |  | U-I ca | unsigned 16 bit |  | 0～359 | 1°
76 | 5451 | 154B | 04 | Read |  | I-I ab | unsigned 16 bit |  | 0～359 | 1°
77 | 5452 | 154C | 04 | Read |  | I-I bc | unsigned 16 bit |  | 0～359 | 1°
78 | 5453 | 154D | 04 | Read |  | I-I ca | unsigned 16 bit |  | 0～359 | 1°
79 | 5454 | 154E | 04 | Read |  | normal phase angle sign | unsigned 16 bit |  | 0:abnormal 1：normal
1、primary voltage=secondary volatge *PT ratio 2、primary current=secondary current *CT ratio 3、primary power=secondary power* PT ratio * CT ratio

## 1XXX Zone Harmonics
Harmonic Parameter
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range | Remarks
1 | 4352 | 1100 | 04 | Read | total harmonic distortion | A line (phase) voltage total harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
2 | 4353 | 1101 | 04 | Read |  | B line (phase) voltage total harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
3 | 4354 | 1102 | 04 | Read |  | C line (phase) voltage total harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
4 | 4355 | 1103 | 04 | Read |  | phase(line)voltage mean total harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
5 | 4356 | 1104 | 04 | Read |  | phase A current total harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
6 | 4357 | 1105 | 04 | Read |  | phase A current total harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
7 | 4358 | 1106 | 04 | Read |  | phase A current total harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
8 | 4359 | 1107 | 04 | Read |  | current mean total harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
9 | 4360 | 1108 | 04 | Read | phase A voltage (odd) harmonic content | phase A line(phase)voltage harmonic ratio（3rd） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
10 | 4361 | 1109 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（5th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
11 | 4362 | 110A | 04 | Read |  | phase A line(phase)voltage harmonic ratio（7th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
12 | 4363 | 110B | 04 | Read |  | phase A line(phase)voltage harmonic ratio（9th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
13 | 4364 | 110C | 04 | Read |  | phase A line(phase)voltage harmonic ratio（11th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
14 | 4365 | 110D | 04 | Read |  | phase A line(phase)voltage harmonic ratio（13th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
15 | 4366 | 110E | 04 | Read |  | phase A line(phase)voltage harmonic ratio（15th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
16 | 4367 | 110F | 04 | Read |  | phase A line(phase)voltage harmonic ratio（17th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
17 | 4368 | 1110 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（19th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
18 | 4369 | 1111 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（21th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
19 | 4370 | 1112 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（13th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
20 | 4371 | 1113 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（25th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
21 | 4372 | 1114 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（27th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
22 | 4373 | 1115 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（29th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
23 | 4374 | 1116 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（31th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
24 | 4375 | 1117 | 04 | Read | phase A voltage (even) harmonic content | phase A line(phase)voltage harmonic ratio（2nd） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
25 | 4376 | 1118 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（4th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
26 | 4377 | 1119 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（6th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
27 | 4378 | 111A | 04 | Read |  | phase A line(phase)voltage harmonic ratio（8th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
28 | 4379 | 111B | 04 | Read |  | phase A line(phase)voltage harmonic ratio（10th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
29 | 4380 | 111C | 04 | Read |  | phase A line(phase)voltage harmonic ratio（12th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
30 | 4381 | 111D | 04 | Read |  | phase A line(phase)voltage harmonic ratio（14th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
31 | 4382 | 111E | 04 | Read |  | phase A line(phase)voltage harmonic ratio（16th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
32 | 4383 | 111F | 04 | Read |  | phase A line(phase)voltage harmonic ratio（18th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
33 | 4384 | 1120 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（20th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
34 | 4385 | 1121 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（22th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
35 | 4386 | 1122 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（24th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
36 | 4387 | 1123 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（26th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
37 | 4388 | 1124 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（28th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
38 | 4389 | 1125 | 04 | Read |  | phase A line(phase)voltage harmonic ratio（30th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
39 | 4390 | 1126 | 04 | Read | phase A volatge harmonic analysis | phase A line(phase)voltage odd harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
40 | 4391 | 1127 | 04 | Read |  | phase A line(phase)voltage even harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
41 | 4392 | 1128 | 04 | Read |  | phase A line(phase)voltage crest factor | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
42 | 4393 | 1129 | 04 | Read |  | reserved | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
43 | 4394 | 112A | 04 | Read | phase B voltage (odd) harmonic content | phase B line(phase)voltage harmonic ratio（3rd） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
44 | 4395 | 112B | 04 | Read |  | phase B line(phase)voltage harmonic ratio（5th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
45 | 4396 | 112C | 04 | Read |  | phase B line(phase)voltage harmonic ratio（7th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
46 | 4397 | 112D | 04 | Read |  | phase B line(phase)voltage harmonic ratio（9th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
47 | 4398 | 112E | 04 | Read |  | phase B line(phase)voltage harmonic ratio（11th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
48 | 4399 | 112F | 04 | Read |  | phase B line(phase)voltage harmonic ratio（13th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
49 | 4400 | 1130 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（15th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
50 | 4401 | 1131 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（17th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
51 | 4402 | 1132 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（19th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
52 | 4403 | 1133 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（21th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
53 | 4404 | 1134 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（13th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
54 | 4405 | 1135 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（25th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
55 | 4406 | 1136 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（27th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
56 | 4407 | 1137 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（29th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
57 | 4408 | 1138 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（31th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
58 | 4409 | 1139 | 04 | Read | phase B voltage (even) harmonic content | phase B line(phase)voltage harmonic ratio（2nd） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
59 | 4410 | 113A | 04 | Read |  | phase B line(phase)voltage harmonic ratio（4th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
60 | 4411 | 113B | 04 | Read |  | phase B line(phase)voltage harmonic ratio（6th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
61 | 4412 | 113C | 04 | Read |  | phase B line(phase)voltage harmonic ratio（8th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
62 | 4413 | 113D | 04 | Read |  | phase B line(phase)voltage harmonic ratio（10th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
63 | 4414 | 113E | 04 | Read |  | phase B line(phase)voltage harmonic ratio（12th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
64 | 4415 | 113F | 04 | Read |  | phase B line(phase)voltage harmonic ratio（14th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
65 | 4416 | 1140 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（16th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
66 | 4417 | 1141 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（18th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
67 | 4418 | 1142 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（20th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
68 | 4419 | 1143 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（22th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
69 | 4420 | 1144 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（24th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
70 | 4421 | 1145 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（26th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
71 | 4422 | 1146 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（28th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
72 | 4423 | 1147 | 04 | Read |  | phase B line(phase)voltage harmonic ratio（30th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
73 | 4424 | 1148 | 04 | Read | phase B volatge harmonic analysis | phase B line(phase)voltage odd harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
74 | 4425 | 1149 | 04 | Read |  | phase B line(phase)voltage even harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
75 | 4426 | 114A | 04 | Read |  | phase B line(phase)voltage crest factor | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
76 | 4427 | 114B | 04 | Read |  | reserved | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
77 | 4428 | 114C | 04 | Read | phase C voltage (odd) harmonic content | phase C line(phase)voltage harmonic ratio（3rd） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
78 | 4429 | 114D | 04 | Read |  | phase C line(phase)voltage harmonic ratio（5th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
79 | 4430 | 114E | 04 | Read |  | phase C line(phase)voltage harmonic ratio（7th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
80 | 4431 | 114F | 04 | Read |  | phase C line(phase)voltage harmonic ratio（9th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
81 | 4432 | 1150 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（11th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
82 | 4433 | 1151 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（13th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
83 | 4434 | 1152 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（15th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
84 | 4435 | 1153 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（17th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
85 | 4436 | 1154 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（19th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
86 | 4437 | 1155 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（21th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
87 | 4438 | 1156 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（13th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
88 | 4439 | 1157 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（25th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
89 | 4440 | 1158 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（27th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
90 | 4441 | 1159 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（29th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
91 | 4442 | 115A | 04 | Read |  | phase C line(phase)voltage harmonic ratio（31th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
92 | 4443 | 115B | 04 | Read | phase C voltage (even) harmonic content | phase C line(phase)voltage harmonic ratio（2nd） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
93 | 4444 | 115C | 04 | Read |  | phase C line(phase)voltage harmonic ratio（4th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
94 | 4445 | 115D | 04 | Read |  | phase C line(phase)voltage harmonic ratio（6th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
95 | 4446 | 115E | 04 | Read |  | phase C line(phase)voltage harmonic ratio（8th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
96 | 4447 | 115F | 04 | Read |  | phase C line(phase)voltage harmonic ratio（10th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
97 | 4448 | 1160 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（12th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
98 | 4449 | 1161 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（14th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
99 | 4450 | 1162 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（16th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
100 | 4451 | 1163 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（18th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
101 | 4452 | 1164 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（20th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
102 | 4453 | 1165 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（22th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
103 | 4454 | 1166 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（24th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
104 | 4455 | 1167 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（26th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
105 | 4456 | 1168 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（28th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
106 | 4457 | 1169 | 04 | Read |  | phase C line(phase)voltage harmonic ratio（30th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
107 | 4458 | 116A | 04 | Read | phase C volatge harmonic analysis | phase C line(phase)voltage odd harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
108 | 4459 | 116B | 04 | Read |  | phase C line(phase)voltage even harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
109 | 4460 | 116C | 04 | Read |  | phase C line(phase)voltage crest factor | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
110 | 4461 | 116D | 04 | Read |  | reserved | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
111 | 4462 | 116E | 04 | Read | phase A current (odd) harmonic content | phase A current harmonic ratio（3rd） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
112 | 4463 | 116F | 04 | Read |  | phase A current harmonic ratio（5th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
113 | 4464 | 1170 | 04 | Read |  | phase A current harmonic ratio（7th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
114 | 4465 | 1171 | 04 | Read |  | phase A current harmonic ratio（9th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
115 | 4466 | 1172 | 04 | Read |  | phase A current harmonic ratio（11th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
116 | 4467 | 1173 | 04 | Read |  | phase A current harmonic ratio（13th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
117 | 4468 | 1174 | 04 | Read |  | phase A current harmonic ratio（15th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
118 | 4469 | 1175 | 04 | Read |  | phase A current harmonic ratio（17th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
119 | 4470 | 1176 | 04 | Read |  | phase A current harmonic ratio（19th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
120 | 4471 | 1177 | 04 | Read |  | phase A current harmonic ratio（21th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
121 | 4472 | 1178 | 04 | Read |  | phase A current harmonic ratio（13th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
122 | 4473 | 1179 | 04 | Read |  | phase A current harmonic ratio（25th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
123 | 4474 | 117A | 04 | Read |  | phase A current harmonic ratio（27th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
124 | 4475 | 117B | 04 | Read |  | phase A current harmonic ratio（29th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
125 | 4476 | 117C | 04 | Read |  | phase A current harmonic ratio（31th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
126 | 4477 | 117D | 04 | Read | phase A current (even) harmonic content | phase A current harmonic ratio（2nd） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
127 | 4478 | 117E | 04 | Read |  | phase A current harmonic ratio（4th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
128 | 4479 | 117F | 04 | Read |  | phase A current harmonic ratio（6th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
129 | 4480 | 1180 | 04 | Read |  | phase A current harmonic ratio（8th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
130 | 4481 | 1181 | 04 | Read |  | phase A current harmonic ratio（104th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
131 | 4482 | 1182 | 04 | Read |  | phase A current harmonic ratio（12th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
132 | 4483 | 1183 | 04 | Read |  | phase A current harmonic ratio（14th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
133 | 4484 | 1184 | 04 | Read |  | phase A current harmonic ratio（16th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
134 | 4485 | 1185 | 04 | Read |  | phase A current harmonic ratio（18th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
135 | 4486 | 1186 | 04 | Read |  | phase A current harmonic ratio（20th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
136 | 4487 | 1187 | 04 | Read |  | phase A current harmonic ratio（22th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
137 | 4488 | 1188 | 04 | Read |  | phase A current harmonic ratio（24th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
138 | 4489 | 1189 | 04 | Read |  | phase A current harmonic ratio（26th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
139 | 4490 | 118A | 04 | Read |  | phase A current harmonic ratio（28th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
140 | 4491 | 118B | 04 | Read |  | phase A current harmonic ratio（30th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
141 | 4492 | 118C | 04 | Read | phase A current harmonic analysis | phase A current odd harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
142 | 4493 | 118D | 04 | Read |  | phase A current even harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
143 | 4494 | 118E | 04 | Read |  | reserved | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
144 | 4495 | 118F | 04 | Read |  | reserved | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
145 | 4496 | 1190 | 04 | Read | phase B current (odd) harmonic content | phase B current harmonic ratio（3rd） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
146 | 4497 | 1191 | 04 | Read |  | phase B current harmonic ratio（5th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
147 | 4498 | 1192 | 04 | Read |  | phase B current harmonic ratio（7th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
148 | 4499 | 1193 | 04 | Read |  | phase B current harmonic ratio（9th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
149 | 4500 | 1194 | 04 | Read |  | phase B current harmonic ratio（11th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
150 | 4501 | 1195 | 04 | Read |  | phase B current harmonic ratio（13th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
151 | 4502 | 1196 | 04 | Read |  | phase B current harmonic ratio（15th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
152 | 4503 | 1197 | 04 | Read |  | phase B current harmonic ratio（17th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
153 | 4504 | 1198 | 04 | Read |  | phase B current harmonic ratio（19th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
154 | 4505 | 1199 | 04 | Read |  | phase B current harmonic ratio（21th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
155 | 4506 | 119A | 04 | Read |  | phase B current harmonic ratio（13th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
156 | 4507 | 119B | 04 | Read |  | phase B current harmonic ratio（25th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
157 | 4508 | 119C | 04 | Read |  | phase B current harmonic ratio（27th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
158 | 4509 | 119D | 04 | Read |  | phase B current harmonic ratio（29th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
159 | 4510 | 119E | 04 | Read |  | phase B current harmonic ratio（31th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
160 | 4511 | 119F | 04 | Read | phase B current (even) harmonic content | phase B current harmonic ratio（2nd） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
161 | 4512 | 11A0 | 04 | Read |  | phase B current harmonic ratio（4th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
162 | 4513 | 11A1 | 04 | Read |  | phase B current harmonic ratio（6th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
163 | 4514 | 11A2 | 04 | Read |  | phase B current harmonic ratio（8th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
164 | 4515 | 11A3 | 04 | Read |  | phase B current harmonic ratio（14th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
165 | 4516 | 11A4 | 04 | Read |  | phase B current harmonic ratio（12th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
166 | 4517 | 11A5 | 04 | Read |  | phase B current harmonic ratio（14th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
167 | 4518 | 11A6 | 04 | Read |  | phase B current harmonic ratio（16th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
168 | 4519 | 11A7 | 04 | Read |  | phase B current harmonic ratio（18th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
169 | 4520 | 11A8 | 04 | Read |  | phase B current harmonic ratio（20th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
170 | 4521 | 11A9 | 04 | Read |  | phase B current harmonic ratio（22th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
171 | 4522 | 11AA | 04 | Read |  | phase B current harmonic ratio（24th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
172 | 4523 | 11AB | 04 | Read |  | phase B current harmonic ratio（26th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
173 | 4524 | 11AC | 04 | Read |  | phase B current harmonic ratio（28th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
174 | 4525 | 11AD | 04 | Read |  | phase B current harmonic ratio（30th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
175 | 4526 | 11AE | 04 | Read | phase B current harmonic analysis | phase B current odd harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
176 | 4527 | 11AF | 04 | Read |  | phase B current even harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
177 | 4528 | 11B0 | 04 | Read |  | reserved | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
178 | 4529 | 11B1 | 04 | Read |  | reserved | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
179 | 4530 | 11B2 | 04 | Read | phase C current (odd) harmonic content | phase C current harmonic ratio（3rd） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
180 | 4531 | 11B3 | 04 | Read |  | phase C current harmonic ratio（5th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
181 | 4532 | 11B4 | 04 | Read |  | phase C current harmonic ratio（7th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
182 | 4533 | 11B5 | 04 | Read |  | phase C current harmonic ratio（9th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
183 | 4534 | 11B6 | 04 | Read |  | phase C current harmonic ratio（11th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
184 | 4535 | 11B7 | 04 | Read |  | phase C current harmonic ratio（13th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
185 | 4536 | 11B8 | 04 | Read |  | phase C current harmonic ratio（15th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
186 | 4537 | 11B9 | 04 | Read |  | phase C current harmonic ratio（17th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
187 | 4538 | 11BA | 04 | Read |  | phase C current harmonic ratio（19th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
188 | 4539 | 11BB | 04 | Read |  | phase C current harmonic ratio（21th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
189 | 4540 | 11BC | 04 | Read |  | phase C current harmonic ratio（13th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
190 | 4541 | 11BD | 04 | Read |  | phase C current harmonic ratio（25th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
191 | 4542 | 11BE | 04 | Read |  | phase C current harmonic ratio（27th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
192 | 4543 | 11BF | 04 | Read |  | phase C current harmonic ratio（29th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
193 | 4544 | 11C0 | 04 | Read |  | phase C current harmonic ratio（31th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
194 | 4545 | 11C1 | 04 | Read | phase C current (even) harmonic content | phase C current harmonic ratio（2nd） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
195 | 4546 | 11C2 | 04 | Read |  | phase C current harmonic ratio（4th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
196 | 4547 | 11C3 | 04 | Read |  | phase C current harmonic ratio（6th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
197 | 4548 | 11C4 | 04 | Read |  | phase C current harmonic ratio（8th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
198 | 4549 | 11C5 | 04 | Read |  | phase C current harmonic ratio（14th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
199 | 4550 | 11C6 | 04 | Read |  | phase C current harmonic ratio（12th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
200 | 4551 | 11C7 | 04 | Read |  | phase C current harmonic ratio（14th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
201 | 4552 | 11C8 | 04 | Read |  | phase C current harmonic ratio（16th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
202 | 4553 | 11C9 | 04 | Read |  | phase C current harmonic ratio（18th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
203 | 4554 | 11CA | 04 | Read |  | phase C current harmonic ratio（20th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
204 | 4555 | 11CB | 04 | Read |  | phase C current harmonic ratio（22th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
205 | 4556 | 11CC | 04 | Read |  | phase C current harmonic ratio（24th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
206 | 4557 | 11CD | 04 | Read |  | phase C current harmonic ratio（26th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
207 | 4558 | 11CE | 04 | Read |  | phase C current harmonic ratio（28th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
208 | 4559 | 11CF | 04 | Read |  | phase C current harmonic ratio（30th） | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
209 | 4560 | 11D0 | 04 | Read | phase C current harmonic analysis | phase C current odd harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
210 | 4561 | 11D1 | 04 | Read |  | phase C current even harmonic distortion | unsigned 16 bit | 0 | 0～10000 | Rx/1000×100%
211 | 4562 | 11D2 | 04 | Read |  | reserved | unsigned 16 bit | 0 |  | Rx/1000×100%
212 | 4563 | 11D3 | 04 | Read |  | reserved | unsigned 16 bit | 0 |  | Rx/1000×100%
“reserved” has no function on register map, just reserved for function extension.

## 2XXX Zone Basic Setting
Basic Parameter Setting
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range |  | Remarks
1 | 8192 | 2000 | 03/06/10 | Read/Write | Basic Parameter | Password Protection (Basic Parameters protection) | unsigned 16 bit | 0 | 0,2～9999 | —— | 1 and 1122 cannot be setted
2 | 8193 | 2001 | 03/06/10 | Read/Write |  | communication address | unsigned 16 bit | 1 | 1～247 | ——
3 | 8194 | 2002 | 03/06/10 | Read/Write |  | 485 communication method | unsigned 16 bit | 0 | 0～2 | —— | 0:8N1 1:8E1 2:8O1
4 | 8195 | 2003 | 03/06/10 | Read/Write |  | 485 baud rate | unsigned 16 bit | 3 | 0～3 | —— | 0:1200,1:2400, 2:4800,3:9600
5 | 8196 | 2004 | 03/06/10 | Read/Write |  | mode of wire connection | unsigned 16 bit | 0 | 0～1 | —— | 0：3 phase 4 wire 1：3 phase 3 wire
6 | 8197 | 2005 | 03/06/10 | Read/Write |  | PT | unsigned 16 bit | 1 | 1～5500 | ——
7 | 8198 | 2006 | 03/06/10 | Read/Write |  | CT | unsigned 16 bit | 1 | 1～50000 | ——
8 | 8199 | 2007 | 03/06/10 | Read/Write |  | CT selection | unsigned 16 bit | 2 | 0～12 | —— | 0:30A,1:80A,2:150A, 3:200A,4:250A,5:400A,6:600A,7:800A,8:1000A,9:1500A,10:2000A, 11:3000A,12:5A
9 | 8200 | 2008 | 03/06/10 | Read/Write |  | secondary rated voltage | unsigned 16 bit | 0 | 0～1 | -- | 0:220V L-N/380V L-L 1:57.7V L-N/100V L-L
10 | 8201 | 2009 | 03/06/10 | Read/Write |  | voltage trend | unsigned 16 bit | 1000 | 100～9999 | V | (Report actively once if the change is greater than the set value, amplify 100 times)
11 | 8202 | 200A | 03/06/10 | Read/Write |  | current trend | unsigned 16 bit | 500 | 50～9999 | A
12 | 8203 | 200B | 03/06/10 | Read/Write |  | temperature trend | unsigned 16 bit | 20 | 5～9999 | ℃
13 | 8204 | 200C | 03/06/10 | Read/Write |  | backlight time | unsigned 16 bit | 40 | 10～999 | second | 0 is always lighting
14 | 8205 | 200D | 03/06/10 | Read/Write |  | Leakage current mode | unsigned 16 bit | 0 | 0～1 | —— | 0：Full wave leakage current 1：Fundamental leakage current
15 | 8206 | 200E | 03/06/10 | Read/Write | Basic Parameter | shielding alarm fault setting | unsigned 16 bit | 0x0000 | 0～0x07ff | —— | 1：shielding（shielding alarm fault, real-time data display）， 0： from low to high, phase A voltage, phase B voltage, phase C voltage, phase A current, phase B current, phase C current, leakage current, temperature A, temperature B, temeprature C, temperature n
16 | 8207 | 200F | 03/06/10 | Read/Write |  | buzzer | unsigned 16 bit | 0 | 0～1 | —— | 0：on 1：off
17 | 8208 | 2010 | 03/06/10 | Read/Write |  | spare | unsigned 16 bit | 0 | 0 | —— | spare register default is 0
18 | 8209 | 2011 | 03/06/10 | Read/Write |  | pulse output | unsigned 16 bit | 0 | 0～3 | —— | 0: no output 1: energy pulse output 2: second pulse 3: fundational reactive energy pulse output
19 | 8210 | 2012 | 03/06/10 | Read/Write |  | protocol symbol | unsigned 16 bit | 0 | 0～3 | —— | 0：MQTT 1:TCPmodbus 2：Custom 3: fault arc
20 | 8211 | 2013 | 03/06/10 | Read/Write |  | master-slave station mode | unsigned 16 bit | 0 | 0～1 | —— | 0：slave station 1：master station
21 | 8212 | 2014 | 03/06/10 | Read/Write |  | RS485 polling time for master station | unsigned 16 bit | 2000 | 100～9999 | millisecond
22 | 8213 | 2015 | 03/06/10 | Read/Write |  | RS485 terminal quantity | unsigned 16 bit | 5 | 0～255 | unit
23 | 8214 | 2016 | 03/06/10 | Read/Write |  | RS485 time out for master station | unsigned 16 bit | 8000 | 1000～9999 | millisecond
24 | 8215 | 2017 | 03/06/10 | Read/Write |  | DO 1 | unsigned 16 bit | 0x80c8 | 5～65535 | —— | (the highest is level /pulse mode，1 is pulse mode，0 is level mode；others are pulse time*10ms)，
25 | 8216 | 2018 | 03/06/10 | Read/Write |  | DO 2 | unsigned 16 bit | 0x80c8 | 5～65535 | ——
26 | 8217 | 2019 | 03/06/10 | Read/Write |  | alarm associated to DO 1 | unsigned 16 bit | 0x01ff | 0～0X1FF | —— | associated according to bit： 0: upper limit of voltage， 1: voltage limit， 2: Voltage Low Limit， 3: Upper current limit， 4: Current Limit， 5: Upper limit of leakage current， 6: leakage current limit， 7: Upper limit of temperature， 8: temperature limit （other bit is valid）
27 | 8218 | 201A | 03/06/10 | Read/Write |  | alarm associated to DO 2 | unsigned 16 bit | 0 | 0～0X1FF | ——
28 | 8219 | 201B | 03/06/10 | Read/Write |  | Data upload interval | unsigned 16 bit | 600 | 20～999 | second
29 | 8220 | 201C | 03/06/10 | Read/Write | Basic Parameter | target ip address 0-1 | unsigned 16 bit | 0x7b3a | 0～65535 | ——
30 | 8221 | 201D | 03/06/10 | Read/Write |  | target ip address 2-3 | unsigned 16 bit | 0xf30d | 0～65535 | ——
31 | 8222 | 201E | 03/06/10 | Read/Write |  | target port number | unsigned 16 bit | 1883 | 0～65535 | ——
32 | 8223 | 201F | 03/06/10 | Read/Write |  | sim card operator | unsigned 16 bit | 0 | 0～3 | —— | Setting APN, 0: Mobile Card， 1：Ordinary Unicom Card，2：Unicom 3G， 3：Telecom Card
33 | 8224 | 2020 | 03/06/10 | Read/Write |  | message timeout | unsigned 16 bit | 10 | 10～9999 | millisecond | not used yet
34 | 8225 | 2021 | 03/06/10 | Read/Write |  | BEATTIM | unsigned 16 bit | 45 | 10～90 | second
35 | 8226 | 2022 | 03/06/10 | Read/Write |  | subscription interval | unsigned 16 bit | 10 | 10～9999 | second
36 | 8227 | 2023 | 03/06/10 | Read/Write |  | alarm interval | unsigned 16 bit | 50 | 10～9999 | second
37 | 8228 | 2024 | 03/06/10 | Read/Write |  | saveday | unsigned 16 bit |  |  |  | not used yet

## 2XXX Zone Multi-Tariff
Multi-tariff Time Setting Zone
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range
1 | 8448 | 2100 | 03/06/10 | Read/Write | multi tariff time setting | Period 1 tariff | unsigned 16 bit | 3 | 1： spike，2： peak 3： flat，4：valley
2 | 8449 | 2101 | 03/06/10 | Read/Write |  | Period 1 start hour、minute | unsigned 16 bit | 7:00 | high bit，hour:0～23 low bit，minute:0～59
3 | 8450 | 2102 | 03/06/10 | Read/Write |  | Period 1 end hour、minute | unsigned 16 bit | 8:00 | high bit，hour:0～23 low bit，minute:0～59
4 | 8451 | 2103 | 03/06/10 | Read/Write |  | Period 2 tariff | unsigned 16 bit | 2 | 1： spike，2： peak 3： flat，4：valley
5 | 8452 | 2104 | 03/06/10 | Read/Write |  | Period 2 start hour、minute | unsigned 16 bit | 8:00 | high bit，hour:0～23 low bit，minute:0～59
6 | 8453 | 2105 | 03/06/10 | Read/Write |  | Period 2 end hour、minute | unsigned 16 bit | 11:00 | high bit，hour:0～23 low bit，minute:0～59
7 | 8454 | 2106 | 03/06/10 | Read/Write |  | Period 3 tariff | unsigned 16 bit | 3 | 1： spike，2： peak 3： flat，4：valley
8 | 8455 | 2107 | 03/06/10 | Read/Write |  | Period 3 start hour、minute | unsigned 16 bit | 11:00 | high bit，hour:0～23 low bit，minute:0～59
9 | 8456 | 2108 | 03/06/10 | Read/Write |  | Period 3 end hour、minute | unsigned 16 bit | 15:00 | high bit，hour:0～23 low bit，minute:0～59
10 | 8457 | 2109 | 03/06/10 | Read/Write |  | Period 4 tariff | unsigned 16 bit | 2 | 1： spike，2： peak 3： flat，4：valley
11 | 8458 | 210A | 03/06/10 | Read/Write |  | Period 4 start hour、minute | unsigned 16 bit | 15:00 | high bit，hour:0～23 low bit，minute:0～59
12 | 8459 | 210B | 03/06/10 | Read/Write |  | Period 4 end hour、minute | unsigned 16 bit | 19:00 | high bit，hour:0～23 low bit，minute:0～59
13 | 8460 | 210C | 03/06/10 | Read/Write |  | Period 5 tariff | unsigned 16 bit | 1 | 1： spike，2： peak 3： flat，4：valley
14 | 8461 | 210D | 03/06/10 | Read/Write |  | Period 5 start hour、minute | unsigned 16 bit | 19:00 | high bit，hour:0～23 low bit，minute:0～59
15 | 8462 | 210E | 03/06/10 | Read/Write |  | Period 5 end hour、minute | unsigned 16 bit | 22:00 | high bit，hour:0～23 low bit，minute:0～59
16 | 8463 | 210F | 03/06/10 | Read/Write |  | Period 6 tariff | unsigned 16 bit | 3 | 1： spike，2： peak 3： flat，4：valley
17 | 8464 | 2110 | 03/06/10 | Read/Write |  | Period 6 start hour、minute | unsigned 16 bit | 22:00 | high bit，hour:0～23 low bit，minute:0～59
18 | 8465 | 2111 | 03/06/10 | Read/Write |  | Period 6 end hour、minute | unsigned 16 bit | 23:00 | high bit，hour:0～23 low bit，minute:0～59
19 | 8466 | 2112 | 03/06/10 | Read/Write |  | Period 7 tariff | unsigned 16 bit | 4 | 1： spike，2： peak 3： flat，4：valley
20 | 8467 | 2113 | 03/06/10 | Read/Write |  | Period 7 start hour、minute | unsigned 16 bit | 23:00 | high bit，hour:0～23 low bit，minute:0～59
21 | 8468 | 2114 | 03/06/10 | Read/Write |  | Period 7 end hour、minute | unsigned 16 bit | 7:00 | high bit，hour:0～23 low bit，minute:0～59
22 | 8469 | 2115 | 03/06/10 | Read/Write |  | Period 8 tariff | unsigned 16 bit | 0 | 1： spike，2： peak 3： flat，4：valley
23 | 8470 | 2116 | 03/06/10 | Read/Write |  | Period 8 start hour、minute | unsigned 16 bit | 0 | high bit，hour:0～23 low bit，minute:0～59
24 | 8471 | 2117 | 03/06/10 | Read/Write |  | Period 8 end hour、minute | unsigned 16 bit | 0 | high bit，hour:0～23 low bit，minute:0～59
25 | 8472 | 2118 | 03/06/10 | Read/Write |  | Period 9 tariff | unsigned 16 bit | 0 | 1： spike，2： peak 3： flat，4：valley
26 | 8473 | 2119 | 03/06/10 | Read/Write |  | Period 9 start hour、minute | unsigned 16 bit | 0 | high bit，hour:0～23 low bit，minute:0～59
27 | 8474 | 211A | 03/06/10 | Read/Write |  | Period 9 end hour、minute | unsigned 16 bit | 0 | high bit，hour:0～23 low bit，minute:0～59
28 | 8475 | 211B | 03/06/10 | Read/Write |  | Period 10 tariff | unsigned 16 bit | 0 | 1： spike，2： peak 3： flat，4：valley
29 | 8476 | 211C | 03/06/10 | Read/Write |  | Period 10 start hour、minute | unsigned 16 bit | 0 | high bit，hour:0～23 low bit，minute:0～59
30 | 8477 | 211D | 03/06/10 | Read/Write |  | Period 10 end hour、minute | unsigned 16 bit | 0 | high bit，hour:0～23 low bit，minute:0～59

## 2XXX Zone Alarm
Alarm Setting Zone
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range |  | Remarks
1 | 8960 | 2300 | 03/06/10 | read/write | Group 1 Alarm Parameter （Phase A voltage upper limit） | Alarm NO | unsigned 16 bit | 0 | 0-15 | ——
2 | 8961 | 2301 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
3 | 8962 | 2302 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 120 | 0-200 | % | PCT
4 | 8963 | 2303 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
5 | 8964 | 2304 |  |  |  | reserved |  | 0
6 | 8965 | 2305 | 03/06/10 | read/write | Group 2 Alarm Parameter （Phase A voltage limit） | Alarm NO | unsigned 16 bit | 1 | 0-15 | ——
7 | 8966 | 2306 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
8 | 8967 | 2307 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 115 | 0-200 | % | PCT
9 | 8968 | 2308 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
10 | 8969 | 2309 | -- | -- |  | reserved |  | 0
11 | 8970 | 230A | 03/06/10 | read/write | Group 3 Alarm Parameter （Phase A voltage lower limit） | Alarm NO | unsigned 16 bit | 2 | 0-15 | ——
12 | 8971 | 230B | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 2 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
13 | 8972 | 230C | 03/06/10 | read/write |  | set value | unsigned 16 bit | 80 | 0-200 | % | PCT
14 | 8973 | 230D | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
15 | 8974 | 230E | -- | -- |  | reserved |  | 0
16 | 8975 | 230F | 03/06/10 | read/write | Group 4 Alarm Parameter （Phase B voltage upper limit） | Alarm NO | unsigned 16 bit | 0 | 0-15 | ——
17 | 8976 | 2310 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
18 | 8977 | 2311 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 120 | 0-200 | % | PCT
19 | 8978 | 2312 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
20 | 8979 | 2313 | -- | -- |  | reserved |  | 0
21 | 8980 | 2314 | 03/06/10 | read/write | Group 5 Alarm Parameter（Phase B voltage limit） | Alarm NO | unsigned 16 bit | 1 | 0-15 | ——
22 | 8981 | 2315 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
23 | 8982 | 2316 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 115 | 0-200 | % | PCT
24 | 8983 | 2317 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
25 | 8984 | 2318 | -- | -- |  | reserved |  | 0
26 | 8985 | 2319 | 03/06/10 | read/write | Group 6 Alarm Parameter （Phase B voltage lower limit） | Alarm NO | unsigned 16 bit | 2 | 0-15 | ——
27 | 8986 | 231A | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 2 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
28 | 8987 | 231B | 03/06/10 | read/write |  | set value | unsigned 16 bit | 80 | 0-200 | % | PCT
29 | 8988 | 231C | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
30 | 8989 | 231D | -- | -- |  | reserved |  | 0
31 | 8990 | 231E | 03/06/10 | read/write | Group 7 Alarm Parameter （Phase C voltage upper limit） | Alarm NO | unsigned 16 bit | 0 | 0-15 | ——
32 | 8991 | 231F | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
33 | 8992 | 2320 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 120 | 0-200 | % | PCT
34 | 8993 | 2321 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
35 | 8994 | 2322 | -- | -- |  | reserved |  | 0
36 | 8995 | 2323 | 03/06/10 | read/write | Group 8 Alarm Parameter （Phase C voltage limit） | Alarm NO | unsigned 16 bit | 1 | 0-15 | ——
37 | 8996 | 2324 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
38 | 8997 | 2325 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 115 | 0-200 | % | PCT
39 | 8998 | 2326 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
40 | 8999 | 2327 | -- | -- |  | reserved |  | 0
41 | 9000 | 2328 | 03/06/10 | read/write | Group 9 Alarm Parameter （Phase C voltage lower limit） | Alarm NO | unsigned 16 bit | 2 | 0-15 | ——
42 | 9001 | 2329 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 2 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
43 | 9002 | 232A | 03/06/10 | read/write |  | set value | unsigned 16 bit | 80 | 0-200 | % | PCT
44 | 9003 | 232B | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
45 | 9004 | 232C | -- | -- |  | reserved |  | 0
46 | 9005 | 232D | 03/06/10 | read/write | Group 10 Alarm Parameter （Phase A current upper limit） | Alarm NO | unsigned 16 bit | 6 | 0-15 | ——
47 | 9006 | 232E | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
48 | 9007 | 232F | 03/06/10 | read/write |  | set value | unsigned 16 bit | 100 | 2-200 | % | PCT
49 | 9008 | 2330 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
50 | 9009 | 2331 | -- | -- |  | reserved |  | 0
51 | 9010 | 2332 | 03/06/10 | read/write | Group 11 Alarm Parameter （Phase A current limit） | Alarm NO | unsigned 16 bit | 7 | 0-15 | ——
52 | 9011 | 2333 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
53 | 9012 | 2334 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 80 | 1-200 | % | PCT
54 | 9013 | 2335 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
55 | 9014 | 2336 | -- | -- |  | reserved |  | 0
56 | 9015 | 2337 | 03/06/10 | read/write | Group 12 Alarm Parameter （Phase B current upper limit） | Alarm NO | unsigned 16 bit | 6 | 0-15 | ——
57 | 9016 | 2338 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
58 | 9017 | 2339 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 100 | 2-200 | % | PCT
59 | 9018 | 233A | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
60 | 9019 | 233B | -- | -- |  | reserved |  | 0
61 | 9020 | 233C | 03/06/10 | read/write | Group 13 Alarm Parameter （Phase B current limit） | Alarm NO | unsigned 16 bit | 7 | 0-15 | ——
62 | 9021 | 233D | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
63 | 9022 | 233E | 03/06/10 | read/write |  | set value | unsigned 16 bit | 80 | 1-200 | % | PCT
64 | 9023 | 233F | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
65 | 9024 | 2340 | -- | -- |  | reserved |  | 0
66 | 9025 | 2341 | 03/06/10 | read/write | Group 14 Alarm Parameter （Phase C current upper limit） | Alarm NO | unsigned 16 bit | 6 | 0-15 | ——
67 | 9026 | 2342 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
68 | 9027 | 2343 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 100 | 2-200 | % | PCT
69 | 9028 | 2344 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
70 | 9029 | 2345 | -- | -- |  | reserved |  | 0
71 | 9030 | 2346 | 03/06/10 | read/write | Group 15 Alarm Parameter （Phase C current limit） | Alarm NO | unsigned 16 bit | 7 | 0-15 | ——
72 | 9031 | 2347 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
73 | 9032 | 2348 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 80 | 1-200 | % | PCT
74 | 9033 | 2349 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
75 | 9034 | 234A | -- | -- |  | reserved |  | 0
76 | 9035 | 234B | 03/06/10 | read/write | Group 16 Alarm Parameter （leakage current upper limit） | Alarm NO | unsigned 16 bit | 6 | 0-15 | ——
77 | 9036 | 234C | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
78 | 9037 | 234D | 03/06/10 | read/write |  | set value | unsigned 16 bit | 3000 | 20-60000 | mA
79 | 9038 | 234E | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
80 | 9039 | 234F | -- | -- |  | reserved |  | 0
81 | 9040 | 2350 | 03/06/10 | read/write | Group 17 Alarm Parameter （leakage current limit） | Alarm NO | unsigned 16 bit | 6 | 0-15 | ——
82 | 9041 | 2351 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
83 | 9042 | 2352 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 1000 | 20-60000 | mA
84 | 9043 | 2353 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
85 | 9044 | 2354 | -- | -- |  | reserved |  | 0
86 | 9045 | 2355 | 03/06/10 | read/write | Group 18 Alarm Parameter （T1 temperature upper limit） | Alarm NO | unsigned 16 bit | 10 | 0-15 | ——
87 | 9046 | 2356 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
88 | 9047 | 2357 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 800 | 450-1400 | ℃ | amplify 10 times
89 | 9048 | 2358 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
90 | 9049 | 2359 | -- | -- |  | reserved |  | 0
91 | 9050 | 235A | 03/06/10 | read/write | Group 19 Alarm Parameter （T1 temperature limit） | Alarm NO | unsigned 16 bit | 11 | 0-15 | ——
92 | 9051 | 235B | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
93 | 9052 | 235C | 03/06/10 | read/write |  | set value | unsigned 16 bit | 600 | 450-1400 | ℃ | amplify 10 times
94 | 9053 | 235D | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
95 | 9054 | 235E | -- | -- |  | reserved |  | 0
96 | 9055 | 235F | 03/06/10 | read/write | Group 20 Alarm Parameter （T2 temperature upper limit） | Alarm NO | unsigned 16 bit | 10 | 0-15 | ——
97 | 9056 | 2360 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
98 | 9057 | 2361 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 800 | 450-1400 | ℃ | amplify 10 times
99 | 9058 | 2362 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
100 | 9059 | 2363 | -- | -- |  | reserved |  | 0
101 | 9060 | 2364 | 03/06/10 | read/write | Group 21 Alarm Parameter （T2 temperature limit） | Alarm NO | unsigned 16 bit | 11 | 0-15 | ——
102 | 9061 | 2365 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
103 | 9062 | 2366 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 600 | 450-1400 | ℃ | amplify 10 times
104 | 9063 | 2367 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
105 | 9064 | 2368 | -- | -- |  | reserved |  | 0
106 | 9065 | 2369 | 03/06/10 | read/write | Group 22 Alarm Parameter （T3 temperature upper limit） | Alarm NO | unsigned 16 bit | 10 | 0-15 | ——
107 | 9066 | 236A | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
108 | 9067 | 236B | 03/06/10 | read/write |  | set value | unsigned 16 bit | 800 | 450-1400 | ℃ | amplify 10 times
109 | 9068 | 236C | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
110 | 9069 | 236D | -- | -- |  | reserved |  | 0
111 | 9070 | 236E | 03/06/10 | read/write | Group 23 Alarm Parameter （T3 temperature limit） | Alarm NO | unsigned 16 bit | 11 | 0-15 | ——
112 | 9071 | 236F | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
113 | 9072 | 2370 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 600 | 450-1400 | ℃ | amplify 10 times
114 | 9073 | 2371 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
115 | 9074 | 2372 | -- | -- |  | reserved |  | 0
116 | 9075 | 2373 | 03/06/10 | read/write | Group 24 Alarm Parameter （T4 temperature upper limit） | Alarm NO | unsigned 16 bit | 10 | 0-15 | ——
117 | 9076 | 2374 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
118 | 9077 | 2375 | 03/06/10 | read/write |  | set value | unsigned 16 bit | 800 | 450-1400 | ℃ | amplify 10 times
119 | 9078 | 2376 | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
120 | 9079 | 2377 | -- | -- |  | reserved |  | 0
121 | 9080 | 2378 | 03/06/10 | read/write | Group 25 Alarm Parameter （T4 temperature limit） | Alarm NO | unsigned 16 bit | 11 | 0-15 | ——
122 | 9081 | 2379 | 03/06/10 | read/write |  | comparison method | unsigned 16 bit | 1 | 0-2 | —— | 0: anergy 1: ＞ 2: ＜
123 | 9082 | 237A | 03/06/10 | read/write |  | set value | unsigned 16 bit | 600 | 450-1400 | ℃ | amplify 10 times
124 | 9083 | 237B | 03/06/10 | read/write |  | delay time | unsigned 16 bit | 40 | 0-5999 | 10ms
125 | 9084 | 237C | -- | -- |  | reserved |  | 0
126 | 9085 | 237D | 03/06/10 | read/write | Group 26 Alarm Parameter | Alarm NO | unsigned 16 bit |  |  |  | Invalid
127 | 9086 | 237E | 03/06/10 | read/write |  | comparison method | unsigned 16 bit
128 | 9087 | 237F | 03/06/10 | read/write |  | set value | unsigned 16 bit
129 | 9088 | 2380 | 03/06/10 | read/write |  | delay time | unsigned 16 bit
130 | 9089 | 2381 | -- | -- |  | reserved
Remark：32 groups can be set, and the first 25 groups are valid Limit：volatge：0%≤lower limit<limit<upper limit≤200%；current：0%≤limit<upper limit≤200%；leakage current：20≤limit<upper limit≤60000；temperature：450≤limit<upper limit≤1400；

## 2XXX Zone MQTT
LORA Parameter Setting
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range |  | Remarks
1 | 8704 | 2200 | 03/06/10 | read/write | LoRa parameter | LoRa channel | unsigned 16 bit | 0 | 0-7 | --
2 | 8705 | 2201 | 03/06/10 | read/write |  | LoRa rate | unsigned 16 bit | 5 | 0-5 | -- | 0:DR0,1:DR1,2:DR2, 3:DR3，4:DR4,5:DR5
3 | 8706 | 2202 | 03/06/10 | read/write |  | LoRa power | unsigned 16 bit | 20 | 5-20 | --
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range |  | Remarks
1 | 9472 | 2500 | -- | -- | Password | The 1st number/letter of domain name | ASCII | 113(q) | 0-127 | --
2 | 9473 | 2501 | -- | -- |  | The 2nd number/letter of domain name | ASCII | 97(a) | 0-127
3 | 9474 | 2502 | -- | -- |  | The 3rd number/letter of domain name | ASCII | 46(.) | 0-127
4 | 9475 | 2503 | -- | -- |  | The 4th number/letter of domain name | ASCII | 109(m) | 0-127
5 | 9476 | 2504 | -- | -- |  | The 5th number/letter of domain name | ASCII | 50(2) | 0-127
6 | 9477 | 2505 | -- | -- |  | The 6th number/letter of domain name | ASCII | 109(m) | 0-127
7 | 9478 | 2506 | -- | -- |  | The 7th number/letter of domain name | ASCII | 46(.) | 0-127
8 | 9479 | 2507 | -- | -- |  | The 8th number/letter of domain name | ASCII | 116(t) | 0-127
9 | 9480 | 2508 | -- | -- |  | The 9th number/letter of domain name | ASCII | 111(o) | 0-127
10 | 9481 | 2509 | -- | -- |  | The10th number/letter of domain name | ASCII | 110(n) | 0-127
11 | 9482 | 250A | -- | -- |  | The 11th number/letter of domain name | ASCII | 103(g) | 0-127
12 | 9483 | 250B | -- | -- |  | The 12th number/letter of domain name | ASCII | 121(y) | 0-127
13 | 9484 | 250C | -- | -- |  | The 13th number/letter of domain name | ASCII | 105(i) | 0-127
14 | 9485 | 250D | -- | -- |  | The 14th number/letter of domain name | ASCII | 46(.) | 0-127
15 | 9486 | 250E | -- | -- |  | The 15th number/letter of domain name | ASCII | 105(i) | 0-127
16 | 9487 | 250F | -- | -- |  | The 16th number/letter of domain name | ASCII | 114(r) | 0-127
17 | 9488 | 2510 | -- | -- | Password | The 17th number/letter of domain name | ASCII | 111(o) | 0-127
18 | 9489 | 2511 | -- | -- |  | The 18th number/letter of domain name | ASCII | 111(o) | 0-127
19 | 9490 | 2512 | -- | -- |  | The 19th number/letter of domain name | ASCII | 116(t) | 0-127
20 | 9491 | 2513 | -- | -- |  | The 20th number/letter of domain name | ASCII | 101(e) | 0-127
21 | 9492 | 2514 | -- | -- |  | The 21th number/letter of domain name | ASCII | 99(c) | 0-127
22 | 9493 | 2515 | -- | -- |  | The 22th number/letter of domain name | ASCII | 104(h) | 0-127
23 | 9494 | 2516 | -- | -- |  | The 23th number/letter of domain name | ASCII | 46(.) | 0-127
24 | 9495 | 2517 | -- | -- |  | The 24th number/letter of domain name | ASCII | 99(c) | 0-127
25 | 9496 | 2518 | -- | -- |  | The 25th number/letter of domain name | ASCII | 111(o) | 0-127
26 | 9497 | 2519 | -- | -- |  | The 26th number/letter of domain name | ASCII | 109(m) | 0-127
27 | 9498 | 251A | -- | -- |  | The 27th number/letter of domain name | ASCII | 0 | 0-127
28 | 9499 | 251B | -- | -- |  | The 28th number/letter of domain name | ASCII | 0 | 0-127
29 | 9500 | 251C | -- | -- |  | The 29th number/letter of domain name | ASCII | 0 | 0-127
30 | 9501 | 251D | -- | -- |  | The 30th number/letter of domain name | ASCII | 0 | 0-127
31 | 9502 | 251E | -- | -- |  | The 31th number/letter of domain name | ASCII | 0 | 0-127
32 | 9503 | 251F | -- | -- |  | The 32th number/letter of domain name | ASCII | 0 | 0-127
33 | 9504 | 2520 | -- | -- | Password | The 33th number/letter of domain name | ASCII | 0 | 0-127
34 | 9505 | 2521 | -- | -- |  | The 34th number/letter of domain name | ASCII | 0 | 0-127
35 | 9506 | 2522 | -- | -- |  | The 35th number/letter of domain name | ASCII | 0 | 0-127
36 | 9507 | 2523 | -- | -- |  | The 36th number/letter of domain name | ASCII | 0 | 0-127
37 | 9508 | 2524 | -- | -- |  | The 37th number/letter of domain name | ASCII | 0 | 0-127
38 | 9509 | 2525 | -- | -- |  | The 38th number/letter of domain name | ASCII | 0 | 0-127
39 | 9510 | 2526 | -- | -- |  | The 39th number/letter of domain name | ASCII | 0 | 0-127
40 | 9511 | 2527 | -- | -- |  | The 40th number/letter of domain name | ASCII | 0 | 0-127
41 | 9512 | 2528 | -- | -- |  | The 41th number/letter of domain name | ASCII | 0 | 0-127
42 | 9513 | 2529 | -- | -- |  | The 42th number/letter of domain name | ASCII | 0 | 0-127
43 | 9514 | 252A | -- | -- |  | The 43th number/letter of domain name | ASCII | 0 | 0-127
44 | 9515 | 252B | -- | -- |  | The 44th number/letter of domain name | ASCII | 0 | 0-127
45 | 9516 | 252C | -- | -- |  | The 45th number/letter of domain name | ASCII | 0 | 0-127
46 | 9517 | 252D | -- | -- |  | The 46th number/letter of domain name | ASCII | 0 | 0-127
47 | 9518 | 252E | -- | -- |  | The 47th number/letter of domain name | ASCII | 0 | 0-127
48 | 9519 | 252F | -- | -- |  | The 48th number/letter of domain name | ASCII | 0 | 0-127
49 | 9520 | 2530 | -- | -- | Password | The 49th number/letter of domain name | ASCII | 0 | 0-127
50 | 9521 | 2531 | -- | -- |  | The 50th number/letter of domain name | ASCII | 0 | 0-127
51 | 9522 | 2532 | -- | -- |  | The 51th number/letter of domain name | ASCII | 0 | 0-127
52 | 9523 | 2533 | -- | -- |  | The 52th number/letter of domain name | ASCII | 0 | 0-127
53 | 9524 | 2534 | -- | -- |  | The 53th number/letter of domain name | ASCII | 0 | 0-127
54 | 9525 | 2535 | -- | -- |  | The 54th number/letter of domain name | ASCII | 0 | 0-127
55 | 9526 | 2536 | -- | -- |  | The 55th number/letter of domain name | ASCII | 0 | 0-127
56 | 9527 | 2537 | -- | -- |  | The 56th number/letter of domain name | ASCII | 0 | 0-127
57 | 9528 | 2538 | -- | -- |  | The 57th number/letter of domain name | ASCII | 0 | 0-127
58 | 9529 | 2539 | -- | -- |  | The 58th number/letter of domain name | ASCII | 0 | 0-127
59 | 9530 | 253A | -- | -- |  | The 59th number/letter of domain name | ASCII | 0 | 0-127
60 | 9531 | 253B | -- | -- |  | The 60th number/letter of domain name | ASCII | 0 | 0-127
61 | 9532 | 253C | -- | -- |  | The 61th number/letter of domain name | ASCII | 0 | 0-127
62 | 9533 | 253D | -- | -- |  | The 62th number/letter of domain name | ASCII | 0 | 0-127
63 | 9534 | 253E | -- | -- |  | The 63th number/letter of domain name | ASCII | 0 | 0-127
64 | 9535 | 253F | -- | -- |  | The 64th number/letter of domain name | ASCII | 0 | 0-127
65 | 9536 | 2540 | -- | -- | Password | The 1st number/letter of password | ASCII | 79(O) | 0-127
66 | 9537 | 2541 | -- | -- |  | The 2nd number/letter of password | ASCII | 113(q) | 0-127
67 | 9538 | 2542 | -- | -- |  | The 3rd number/letter of password | ASCII | 89(Y) | 0-127
68 | 9539 | 2543 | -- | -- |  | The 4th umber/letter of password | ASCII | 47(/) | 0-127
69 | 9540 | 2544 | -- | -- |  | The 5th umber/letter of password | ASCII | 79(O) | 0-127
70 | 9541 | 2545 | -- | -- |  | The 6th umber/letter of password | ASCII | 55(7) | 0-127
71 | 9542 | 2546 | -- | -- |  | The 7th umber/letter of password | ASCII | 65(A) | 0-127
72 | 9543 | 2547 | -- | -- |  | The 8th umber/letter of password | ASCII | 110(n) | 0-127
73 | 9544 | 2548 | -- | -- |  | The 9th umber/letter of password | ASCII | 98(b) | 0-127
74 | 9545 | 2549 | -- | -- |  | The 10th umber/letter of password | ASCII | 70(F) | 0-127
75 | 9546 | 254A | -- | -- |  | The 11th umber/letter of password | ASCII | 55(7) | 0-127
76 | 9547 | 254B | -- | -- |  | The 12th umber/letter of password | ASCII | 68(D) | 0-127
77 | 9548 | 254C | -- | -- |  | The 13th umber/letter of password | ASCII | 51(3) | 0-127
78 | 9549 | 254D | -- | -- |  | The 14th umber/letter of password | ASCII | 107(k) | 0-127
79 | 9550 | 254E | -- | -- |  | The 15th umber/letter of password | ASCII | 111(o) | 0-127
80 | 9551 | 254F | -- | -- |  | The 16th umber/letter of password | ASCII | 51(3) | 0-127
81 | 9552 | 2550 | -- | -- | Password | The 17th umber/letter of password | ASCII | 83(S) | 0-127
82 | 9553 | 2551 | -- | -- |  | The 18th umber/letter of password | ASCII | 56(8) | 0-127
83 | 9554 | 2552 | -- | -- |  | The 19th umber/letter of password | ASCII | 85(U) | 0-127
84 | 9555 | 2553 | -- | -- |  | The 20th umber/letter of password | ASCII | 80(P) | 0-127
85 | 9556 | 2554 | -- | -- |  | The 21th umber/letter of password | ASCII | 109(m) | 0-127
86 | 9557 | 2555 | -- | -- |  | The 22th umber/letter of password | ASCII | 81(Q) | 0-127
87 | 9558 | 2556 | -- | -- |  | The 23th umber/letter of password | ASCII | 61(=) | 0-127
88 | 9559 | 2557 | -- | -- |  | The 24th umber/letter of password | ASCII | 61(=) | 0-127
89 | 9560 | 2558 | -- | -- |  | The 25th umber/letter of password | ASCII | 0 | 0-127
90 | 9561 | 2559 | -- | -- |  | The 26th umber/letter of password | ASCII | 0 | 0-127
91 | 9562 | 255A | -- | -- |  | The 27th umber/letter of password | ASCII | 0 | 0-127
92 | 9563 | 255B | -- | -- |  | The 28th umber/letter of password | ASCII | 0 | 0-127
93 | 9564 | 255C | -- | -- |  | The 29th umber/letter of password | ASCII | 0 | 0-127
94 | 9565 | 255D | -- | -- |  | The 30th umber/letter of password | ASCII | 0 | 0-127
95 | 9566 | 255E | -- | -- |  | The 31th umber/letter of password | ASCII | 0 | 0-127
96 | 9567 | 255F | -- | -- |  | The 32th umber/letter of password | ASCII | 0 | 0-127

## 3XXX Zone
Alarm Status Zone
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range |  | Remark
1 | 12288 | 3000 | 03 | read | status | Alarm Status | unsigned 16 bit | 0 | 0～65535 | -- | Alarm status 1 (from low bit to high bit): phase A voltage upper limit alarm, limit alarm, lower limit; phase B voltage upper limit alarm, limit alarm, lower limit; phase C voltage upper limit alarm, limit alarm, lower limit; phase A current upper limit alarm, limit alarm; phase B current upper limit alarm, limit alarm; phase C current upper limit alarm, limit alarm; leakage current upper limit alarm
2 | 12289 | 3001 | 03 | read |  | Alarm Status | unsigned 16 bit | 0 | 0～65535 | -- | Alarm status 2 (from low bit to high bit): leakage current limit alarm;T1 temperature upper limit alarm, limit alarm;T2 temperature upper limit alarm, limit alarm;T3 temperature upper limit alarm, limit alarm;T4 temperature upper limit alarm, limit alarm.
3 | 12290 | 3002 | 03 | read |  | Alarm Status | unsigned 16 bit | 0 | 0～65535 | -- | Fault status(from low bit to high bit)：Leakage current short circuit，Leakage circuit breaker; T1 temperature short circuit，T1 temperature breaker; T2 temperature short circuit，T2 temperature breaker; T3 temperature short circuit，T3 temperature breaker; T4 temperature short circuit，T4 temperature breaker;
Real-time Clock Zone
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range |  | Remark
1 | 12800 | 3200 | 03/06/10 | read/write | time | year | unsigned 16 bit | 2000 | 2000～2099 | year
2 | 12801 | 3201 | 03/06/10 | read/write |  | month | unsigned 16 bit | 1 | 1～12 | month
3 | 12802 | 3202 | 03/06/10 | read/write |  | day | unsigned 16 bit | 1 | 1～31 | day
4 | 12803 | 3203 | 03/06/10 | read/write |  | hour | unsigned 16 bit | 0 | 0～23 | hour
5 | 12804 | 3204 | 03/06/10 | read/write |  | minute | unsigned 16 bit | 0 | 0～59 | minute
6 | 12805 | 3205 | 03/06/10 | read/write |  | second | unsigned 16 bit | 0 | 0～59 | second
7 | 12806 | 3206 | 03/06/10 | read/write |  | millsecond | unsigned 16 bit | 0 | 0～999 | millsecond

## 4XXX Zone Real-Time Data
Real-time Energy Zone
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameter |  | Data Type | Default | Value Range |  | Remark
1 | 16384 | 4000 | 04 | read | real-time energy | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
2 | 16385 | 4001 | 04 | read
3 | 16386 | 4002 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
4 | 16387 | 4003 | 04 | read
5 | 16388 | 4004 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
6 | 16389 | 4005 | 04 | read
7 | 16390 | 4006 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
8 | 16391 | 4007 | 04 | read
9 | 16392 | 4008 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
10 | 16393 | 4009 | 04 | read
11 | 16394 | 400A | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
12 | 16395 | 400B | 04 | read
Real-time Pulse Energy Zone
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range |  | Remark
1 | 17664 | 4500 | 04 | read | energy pulse | forward active energy pulse number | unsigned 64 bit | 0 |  | ——
2 | 17665 | 4501 | 04 | read
3 | 17666 | 4502 | 04 | read
4 | 17667 | 4503 | 04 | read
5 | 17668 | 4504 | 04 | read |  | reversing active energy pulse number | unsigned 64 bit | 0 |  | ——
6 | 17669 | 4505 | 04 | read
7 | 17670 | 4506 | 04 | read
8 | 17671 | 4507 | 04 | read
9 | 17672 | 4508 | 04 | read |  | forward reactive energy pulse number | unsigned 64 bit | 0 |  | ——
10 | 17673 | 4509 | 04 | read
11 | 17674 | 450A | 04 | read
12 | 17675 | 450B | 04 | read
13 | 17676 | 450C | 04 | read |  | reversing reactive energy pulse number | unsigned 64 bit | 0 |  | ——
14 | 17677 | 450D | 04 | read
15 | 17678 | 450E | 04 | read
16 | 17679 | 450F | 04 | read
Max. Demand
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range |  | Remark
1 | 17920 | 4600 | 04 | read | day max. demand | day demand | unsigned 32 bit | 0 | 0-4294967295 | kW
2 | 17921 | 4601 | 04 | read
3 | 17922 | 4602 | 04 | read |  | day demand time（year，second） | unsigned 16 bit | 0 | 0-65535
4 | 17923 | 4603 | 04 | read |  | day demand time（month，day） | unsigned 16 bit | 0 | 0-65535
5 | 17924 | 4604 | 04 | read |  | day demand time（hour，minute） | unsigned 16 bit | 0 | 0-65535
6 | 17925 | 4605 | 04 | read | last day max. demand | last day demand | unsigned 32 bit | 0 | 0-4294967295 | kW
7 | 17926 | 4606 | 04 | read
8 | 17927 | 4607 | 04 | read |  | last day demand time（year，second） | unsigned 16 bit | 0 | 0-65535
9 | 17928 | 4608 | 04 | read |  | last day demand time（month，day） | unsigned 16 bit | 0 | 0-65535
10 | 17929 | 4609 | 04 | read |  | last day demand time（hour，minute） | unsigned 16 bit | 0 | 0-65535
11 | 17930 | 460A | 04 | read | month max. demand | month demand | unsigned 32 bit | 0 | 0-4294967295 | kW
12 | 17931 | 460B | 04 | read
13 | 17932 | 460C | 04 | read |  | month demand time（year，second） | unsigned 16 bit | 0 | 0-65535
14 | 17933 | 460D | 04 | read |  | month demand time（month，day） | unsigned 16 bit | 0 | 0-65535
15 | 17934 | 460E | 04 | read |  | month demand time（hour，minute） | unsigned 16 bit | 0 | 0-65535
16 | 17935 | 460F | 04 | read | last month demand | last month demand | unsigned 32 bit | 0 | 0-4294967295 | kW
17 | 17936 | 4610 | 04 | read
18 | 17937 | 4611 | 04 | read |  | last month demand time（year，second） | unsigned 16 bit | 0 | 0-65535
19 | 17938 | 4612 | 04 | read |  | last month demand time（month，day） | unsigned 16 bit | 0 | 0-65535
20 | 17939 | 4613 | 04 | read |  | last month demand time（hour，minute） | unsigned 16 bit | 0 | 0-65535

## 4XXX Zone Historical Data
Multi-tariff historical energy zone
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range |  | Remark
1 | 16640 | 4100 | 04 | read | current month total | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
2 | 16641 | 4101 | 04 | read
3 | 16642 | 4102 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
4 | 16643 | 4103 | 04 | read
5 | 16644 | 4104 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
6 | 16645 | 4105 | 04 | read
7 | 16646 | 4106 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
8 | 16647 | 4107 | 04 | read
9 | 16648 | 4108 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
10 | 16649 | 4109 | 04 | read
11 | 16650 | 410A | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
12 | 16651 | 410B | 04 | read
13 | 16652 | 410C | 04 | read | current month spike | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
14 | 16653 | 410D | 04 | read
15 | 16654 | 410E | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
16 | 16655 | 410F | 04 | read
17 | 16656 | 4110 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
18 | 16657 | 4111 | 04 | read
19 | 16658 | 4112 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
20 | 16659 | 4113 | 04 | read
21 | 16660 | 4114 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
22 | 16661 | 4115 | 04 | read
23 | 16662 | 4116 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
24 | 16663 | 4117 | 04 | read
25 | 16664 | 4118 | 04 | read | current month peak | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
26 | 16665 | 4119 | 04 | read
27 | 16666 | 411A | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
28 | 16667 | 411B | 04 | read
29 | 16668 | 411C | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
30 | 16669 | 411D | 04 | read
31 | 16670 | 411E | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
32 | 16671 | 411F | 04 | read
33 | 16672 | 4120 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
34 | 16673 | 4121 | 04 | read
35 | 16674 | 4122 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
36 | 16675 | 4123 | 04 | read
37 | 16676 | 4124 | 04 | read | current month flat | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
38 | 16677 | 4125 | 04 | read
39 | 16678 | 4126 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
40 | 16679 | 4127 | 04 | read
41 | 16680 | 4128 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
42 | 16681 | 4129 | 04 | read
43 | 16682 | 412A | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
44 | 16683 | 412B | 04 | read
45 | 16684 | 412C | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
46 | 16685 | 412D | 04 | read
47 | 16686 | 412E | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
48 | 16687 | 412F | 04 | read
49 | 16688 | 4130 | 04 | read | current month valley | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
50 | 16689 | 4131 | 04 | read
51 | 16690 | 4132 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
52 | 16691 | 4133 | 04 | read
53 | 16692 | 4134 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
54 | 16693 | 4135 | 04 | read
55 | 16694 | 4136 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
56 | 16695 | 4137 | 04 | read
57 | 16696 | 4138 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
58 | 16697 | 4139 | 04 | read
59 | 16698 | 413A | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
60 | 16699 | 413B | 04 | read
61 | 16700 | 413C | 04 | read | last 1 month total | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
62 | 16701 | 413D | 04 | read
63 | 16702 | 413E | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
64 | 16703 | 413F | 04 | read
65 | 16704 | 4140 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
66 | 16705 | 4141 | 04 | read
67 | 16706 | 4142 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
68 | 16707 | 4143 | 04 | read
69 | 16708 | 4144 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
70 | 16709 | 4145 | 04 | read
71 | 16710 | 4146 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
72 | 16711 | 4147 | 04 | read
73 | 16712 | 4148 | 04 | read | last 1 month spike | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
74 | 16713 | 4149 | 04 | read
75 | 16714 | 414A | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
76 | 16715 | 414B | 04 | read
77 | 16716 | 414C | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
78 | 16717 | 414D | 04 | read
79 | 16718 | 414E | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
80 | 16719 | 414F | 04 | read
81 | 16720 | 4150 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
82 | 16721 | 4151 | 04 | read
83 | 16722 | 4152 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
84 | 16723 | 4153 | 04 | read
85 | 16724 | 4154 | 04 | read | last 1 month peak | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
86 | 16725 | 4155 | 04 | read
87 | 16726 | 4156 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
88 | 16727 | 4157 | 04 | read
89 | 16728 | 4158 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
90 | 16729 | 4159 | 04 | read
91 | 16730 | 415A | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
92 | 16731 | 415B | 04 | read
93 | 16732 | 415C | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
94 | 16733 | 415D | 04 | read
95 | 16734 | 415E | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
96 | 16735 | 415F | 04 | read
97 | 16736 | 4160 | 04 | read | last 1 month flat | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
98 | 16737 | 4161 | 04 | read
99 | 16738 | 4162 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
100 | 16739 | 4163 | 04 | read
101 | 16740 | 4164 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
102 | 16741 | 4165 | 04 | read
103 | 16742 | 4166 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
104 | 16743 | 4167 | 04 | read
105 | 16744 | 4168 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
106 | 16745 | 4169 | 04 | read
107 | 16746 | 416A | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
108 | 16747 | 416B | 04 | read
109 | 16748 | 416C | 04 | read | last 1 month valley | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
110 | 16749 | 416D | 04 | read
111 | 16750 | 416E | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
112 | 16751 | 416F | 04 | read
113 | 16752 | 4170 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
114 | 16753 | 4171 | 04 | read
115 | 16754 | 4172 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
116 | 16755 | 4173 | 04 | read
117 | 16756 | 4174 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
118 | 16757 | 4175 | 04 | read
119 | 16758 | 4176 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
120 | 16759 | 4177 | 04 | read
121 | 16760 | 4178 | 04 | read | last 2 month total | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
122 | 16761 | 4179 | 04 | read
123 | 16762 | 417A | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
124 | 16763 | 417B | 04 | read
125 | 16764 | 417C | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
126 | 16765 | 417D | 04 | read
127 | 16766 | 417E | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
128 | 16767 | 417F | 04 | read
129 | 16768 | 4180 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
130 | 16769 | 4181 | 04 | read
131 | 16770 | 4182 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
132 | 16771 | 4183 | 04 | read
133 | 16772 | 4184 | 04 | read | last 2 month spike | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
134 | 16773 | 4185 | 04 | read
135 | 16774 | 4186 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
136 | 16775 | 4187 | 04 | read
137 | 16776 | 4188 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
138 | 16777 | 4189 | 04 | read
139 | 16778 | 418A | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
140 | 16779 | 418B | 04 | read
141 | 16780 | 418C | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
142 | 16781 | 418D | 04 | read
143 | 16782 | 418E | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
144 | 16783 | 418F | 04 | read
145 | 16784 | 4190 | 04 | read | last 2 month peak | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
146 | 16785 | 4191 | 04 | read
147 | 16786 | 4192 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
148 | 16787 | 4193 | 04 | read
149 | 16788 | 4194 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
150 | 16789 | 4195 | 04 | read
151 | 16790 | 4196 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
152 | 16791 | 4197 | 04 | read
153 | 16792 | 4198 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
154 | 16793 | 4199 | 04 | read
155 | 16794 | 419A | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
156 | 16795 | 419B | 04 | read
157 | 16796 | 419C | 04 | read | last 2 month flat | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
158 | 16797 | 419D | 04 | read
159 | 16798 | 419E | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
160 | 16799 | 419F | 04 | read
161 | 16800 | 41A0 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
162 | 16801 | 41A1 | 04 | read
163 | 16802 | 41A2 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
164 | 16803 | 41A3 | 04 | read
165 | 16804 | 41A4 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
166 | 16805 | 41A5 | 04 | read
167 | 16806 | 41A6 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
168 | 16807 | 41A7 | 04 | read
169 | 16808 | 41A8 | 04 | read | last 2 month valley | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
170 | 16809 | 41A9 | 04 | read
171 | 16810 | 41AA | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
172 | 16811 | 41AB | 04 | read
173 | 16812 | 41AC | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
174 | 16813 | 41AD | 04 | read
175 | 16814 | 41AE | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
176 | 16815 | 41AF | 04 | read
177 | 16816 | 41B0 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
178 | 16817 | 41B1 | 04 | read
179 | 16818 | 41B2 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
180 | 16819 | 41B3 | 04 | read
181 | 16820 | 41B4 | 04 | read | last 3 month total | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
182 | 16821 | 41B5 | 04 | read
183 | 16822 | 41B6 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
184 | 16823 | 41B7 | 04 | read
185 | 16824 | 41B8 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
186 | 16825 | 41B9 | 04 | read
187 | 16826 | 41BA | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
188 | 16827 | 41BB | 04 | read
189 | 16828 | 41BC | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
190 | 16829 | 41BD | 04 | read
191 | 16830 | 41BE | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
192 | 16831 | 41BF | 04 | read
193 | 16832 | 41C0 | 04 | read | last 3 month spike | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
194 | 16833 | 41C1 | 04 | read
195 | 16834 | 41C2 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
196 | 16835 | 41C3 | 04 | read
197 | 16836 | 41C4 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
198 | 16837 | 41C5 | 04 | read
199 | 16838 | 41C6 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
200 | 16839 | 41C7 | 04 | read
201 | 16840 | 41C8 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
202 | 16841 | 41C9 | 04 | read
203 | 16842 | 41CA | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
204 | 16843 | 41CB | 04 | read
205 | 16844 | 41CC | 04 | read | last 3 month peak | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
206 | 16845 | 41CD | 04 | read
207 | 16846 | 41CE | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
208 | 16847 | 41CF | 04 | read
209 | 16848 | 41D0 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
210 | 16849 | 41D1 | 04 | read
211 | 16850 | 41D2 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
212 | 16851 | 41D3 | 04 | read
213 | 16852 | 41D4 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
214 | 16853 | 41D5 | 04 | read
215 | 16854 | 41D6 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
216 | 16855 | 41D7 | 04 | read
217 | 16856 | 41D8 | 04 | read | last 3 month flat | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
218 | 16857 | 41D9 | 04 | read
219 | 16858 | 41DA | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
220 | 16859 | 41DB | 04 | read
221 | 16860 | 41DC | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
222 | 16861 | 41DD | 04 | read
223 | 16862 | 41DE | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
224 | 16863 | 41DF | 04 | read
225 | 16864 | 41E0 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
226 | 16865 | 41E1 | 04 | read
227 | 16866 | 41E2 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
228 | 16867 | 41E3 | 04 | read
229 | 16868 | 41E4 | 04 | read | last 3 month valley | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
230 | 16869 | 41E5 | 04 | read
231 | 16870 | 41E6 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
232 | 16871 | 41E7 | 04 | read
233 | 16872 | 41E8 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
234 | 16873 | 41E9 | 04 | read
235 | 16874 | 41EA | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
236 | 16875 | 41EB | 04 | read
237 | 16876 | 41EC | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
238 | 16877 | 41ED | 04 | read
239 | 16878 | 41EE | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
240 | 16879 | 41EF | 04 | read
241 | 16880 | 41F0 | 04 | read | last 4 month total | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
242 | 16881 | 41F1 | 04 | read
243 | 16882 | 41F2 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
244 | 16883 | 41F3 | 04 | read
245 | 16884 | 41F4 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
246 | 16885 | 41F5 | 04 | read
247 | 16886 | 41F6 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
248 | 16887 | 41F7 | 04 | read
249 | 16888 | 41F8 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
250 | 16889 | 41F9 | 04 | read
251 | 16890 | 41FA | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
252 | 16891 | 41FB | 04 | read
253 | 16892 | 41FC | 04 | read | last 4 month spike | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
254 | 16893 | 41FD | 04 | read
255 | 16894 | 41FE | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
256 | 16895 | 41FF | 04 | read
257 | 16896 | 4200 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
258 | 16897 | 4201 | 04 | read
259 | 16898 | 4202 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
260 | 16899 | 4203 | 04 | read
261 | 16900 | 4204 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
262 | 16901 | 4205 | 04 | read
263 | 16902 | 4206 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
264 | 16903 | 4207 | 04 | read
265 | 16904 | 4208 | 04 | read | last 4 month peak | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
266 | 16905 | 4209 | 04 | read
267 | 16906 | 420A | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
268 | 16907 | 420B | 04 | read
269 | 16908 | 420C | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
270 | 16909 | 420D | 04 | read
271 | 16910 | 420E | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
272 | 16911 | 420F | 04 | read
273 | 16912 | 4210 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
274 | 16913 | 4211 | 04 | read
275 | 16914 | 4212 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
276 | 16915 | 4213 | 04 | read
277 | 16916 | 4214 | 04 | read | last 4 month flat | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
278 | 16917 | 4215 | 04 | read
279 | 16918 | 4216 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
280 | 16919 | 4217 | 04 | read
281 | 16920 | 4218 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
282 | 16921 | 4219 | 04 | read
283 | 16922 | 421A | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
284 | 16923 | 421B | 04 | read
285 | 16924 | 421C | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
286 | 16925 | 421D | 04 | read
287 | 16926 | 421E | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
288 | 16927 | 421F | 04 | read
289 | 16928 | 4220 | 04 | read | last 4 month valley | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
290 | 16929 | 4221 | 04 | read
291 | 16930 | 4222 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
292 | 16931 | 4223 | 04 | read
293 | 16932 | 4224 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
294 | 16933 | 4225 | 04 | read
295 | 16934 | 4226 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
296 | 16935 | 4227 | 04 | read
297 | 16936 | 4228 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
298 | 16937 | 4229 | 04 | read
299 | 16938 | 422A | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
300 | 16939 | 422B | 04 | read
301 | 16940 | 422C | 04 | read | last 5 month total | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
302 | 16941 | 422D | 04 | read
303 | 16942 | 422E | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
304 | 16943 | 422F | 04 | read
305 | 16944 | 4230 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
306 | 16945 | 4231 | 04 | read
307 | 16946 | 4232 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
308 | 16947 | 4233 | 04 | read
309 | 16948 | 4234 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
310 | 16949 | 4235 | 04 | read
311 | 16950 | 4236 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
312 | 16951 | 4237 | 04 | read
313 | 16952 | 4238 | 04 | read | last 5 month spike | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
314 | 16953 | 4239 | 04 | read
315 | 16954 | 423A | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
316 | 16955 | 423B | 04 | read
317 | 16956 | 423C | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
318 | 16957 | 423D | 04 | read
319 | 16958 | 423E | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
320 | 16959 | 423F | 04 | read
321 | 16960 | 4240 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
322 | 16961 | 4241 | 04 | read
323 | 16962 | 4242 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
324 | 16963 | 4243 | 04 | read
325 | 16964 | 4244 | 04 | read | last 5 month peak | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
326 | 16965 | 4245 | 04 | read
327 | 16966 | 4246 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
328 | 16967 | 4247 | 04 | read
329 | 16968 | 4248 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
330 | 16969 | 4249 | 04 | read
331 | 16970 | 424A | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
332 | 16971 | 424B | 04 | read
333 | 16972 | 424C | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
334 | 16973 | 424D | 04 | read
335 | 16974 | 424E | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
336 | 16975 | 424F | 04 | read
337 | 16976 | 4250 | 04 | read | last 5 month flat | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
338 | 16977 | 4251 | 04 | read
339 | 16978 | 4252 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
340 | 16979 | 4253 | 04 | read
341 | 16980 | 4254 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
342 | 16981 | 4255 | 04 | read
343 | 16982 | 4256 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
344 | 16983 | 4257 | 04 | read
345 | 16984 | 4258 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
346 | 16985 | 4259 | 04 | read
347 | 16986 | 425A | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
348 | 16987 | 425B | 04 | read
349 | 16988 | 425C | 04 | read | last 5 month valley | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
350 | 16989 | 425D | 04 | read
351 | 16990 | 425E | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
352 | 16991 | 425F | 04 | read
353 | 16992 | 4260 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
354 | 16993 | 4261 | 04 | read
355 | 16994 | 4262 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
356 | 16995 | 4263 | 04 | read
357 | 16996 | 4264 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
358 | 16997 | 4265 | 04 | read
359 | 16998 | 4266 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
360 | 16999 | 4267 | 04 | read
361 | 17000 | 4268 | 04 | read | last 6 month total | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
362 | 17001 | 4269 | 04 | read
363 | 17002 | 426A | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
364 | 17003 | 426B | 04 | read
365 | 17004 | 426C | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
366 | 17005 | 426D | 04 | read
367 | 17006 | 426E | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
368 | 17007 | 426F | 04 | read
369 | 17008 | 4270 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
370 | 17009 | 4271 | 04 | read
371 | 17010 | 4272 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
372 | 17011 | 4273 | 04 | read
373 | 17012 | 4274 | 04 | read | last 6 month spike | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
374 | 17013 | 4275 | 04 | read
375 | 17014 | 4276 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
376 | 17015 | 4277 | 04 | read
377 | 17016 | 4278 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
378 | 17017 | 4279 | 04 | read
379 | 17018 | 427A | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
380 | 17019 | 427B | 04 | read
381 | 17020 | 427C | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
382 | 17021 | 427D | 04 | read
383 | 17022 | 427E | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
384 | 17023 | 427F | 04 | read
385 | 17024 | 4280 | 04 | read | last 6 month peak | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
386 | 17025 | 4281 | 04 | read
387 | 17026 | 4282 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
388 | 17027 | 4283 | 04 | read
389 | 17028 | 4284 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
390 | 17029 | 4285 | 04 | read
391 | 17030 | 4286 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
392 | 17031 | 4287 | 04 | read
393 | 17032 | 4288 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
394 | 17033 | 4289 | 04 | read
395 | 17034 | 428A | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
396 | 17035 | 428B | 04 | read
397 | 17036 | 428C | 04 | read | last 6 month flat | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
398 | 17037 | 428D | 04 | read
399 | 17038 | 428E | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
400 | 17039 | 428F | 04 | read
401 | 17040 | 4290 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
402 | 17041 | 4291 | 04 | read
403 | 17042 | 4292 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
404 | 17043 | 4293 | 04 | read
405 | 17044 | 4294 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
406 | 17045 | 4295 | 04 | read
407 | 17046 | 4296 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
408 | 17047 | 4297 | 04 | read
409 | 17048 | 4298 | 04 | read | last 6 month valley | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
410 | 17049 | 4299 | 04 | read
411 | 17050 | 429A | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
412 | 17051 | 429B | 04 | read
413 | 17052 | 429C | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
414 | 17053 | 429D | 04 | read
415 | 17054 | 429E | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
416 | 17055 | 429F | 04 | read
417 | 17056 | 42A0 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
418 | 17057 | 42A1 | 04 | read
419 | 17058 | 42A2 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
420 | 17059 | 42A3 | 04 | read
421 | 17060 | 42A4 | 04 | read | last 7 month total | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
422 | 17061 | 42A5 | 04 | read
423 | 17062 | 42A6 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
424 | 17063 | 42A7 | 04 | read
425 | 17064 | 42A8 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
426 | 17065 | 42A9 | 04 | read
427 | 17066 | 42AA | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
428 | 17067 | 42AB | 04 | read
429 | 17068 | 42AC | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
430 | 17069 | 42AD | 04 | read
431 | 17070 | 42AE | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
432 | 17071 | 42AF | 04 | read
433 | 17072 | 42B0 | 04 | read | last 7 month spike | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
434 | 17073 | 42B1 | 04 | read
435 | 17074 | 42B2 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
436 | 17075 | 42B3 | 04 | read
437 | 17076 | 42B4 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
438 | 17077 | 42B5 | 04 | read
439 | 17078 | 42B6 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
440 | 17079 | 42B7 | 04 | read
441 | 17080 | 42B8 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
442 | 17081 | 42B9 | 04 | read
443 | 17082 | 42BA | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
444 | 17083 | 42BB | 04 | read
445 | 17084 | 42BC | 04 | read | last 7 month peak | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
446 | 17085 | 42BD | 04 | read
447 | 17086 | 42BE | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
448 | 17087 | 42BF | 04 | read
449 | 17088 | 42C0 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
450 | 17089 | 42C1 | 04 | read
451 | 17090 | 42C2 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
452 | 17091 | 42C3 | 04 | read
453 | 17092 | 42C4 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
454 | 17093 | 42C5 | 04 | read
455 | 17094 | 42C6 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
456 | 17095 | 42C7 | 04 | read
457 | 17096 | 42C8 | 04 | read | last 7 month flat | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
458 | 17097 | 42C9 | 04 | read
459 | 17098 | 42CA | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
460 | 17099 | 42CB | 04 | read
461 | 17100 | 42CC | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
462 | 17101 | 42CD | 04 | read
463 | 17102 | 42CE | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
464 | 17103 | 42CF | 04 | read
465 | 17104 | 42D0 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
466 | 17105 | 42D1 | 04 | read
467 | 17106 | 42D2 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
468 | 17107 | 42D3 | 04 | read
469 | 17108 | 42D4 | 04 | read | last 7 month valley | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
470 | 17109 | 42D5 | 04 | read
471 | 17110 | 42D6 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
472 | 17111 | 42D7 | 04 | read
473 | 17112 | 42D8 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
474 | 17113 | 42D9 | 04 | read
475 | 17114 | 42DA | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
476 | 17115 | 42DB | 04 | read
477 | 17116 | 42DC | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
478 | 17117 | 42DD | 04 | read
479 | 17118 | 42DE | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
480 | 17119 | 42DF | 04 | read
481 | 17120 | 42E0 | 04 | read | last 8 month total | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
482 | 17121 | 42E1 | 04 | read
483 | 17122 | 42E2 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
484 | 17123 | 42E3 | 04 | read
485 | 17124 | 42E4 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
486 | 17125 | 42E5 | 04 | read
487 | 17126 | 42E6 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
488 | 17127 | 42E7 | 04 | read
489 | 17128 | 42E8 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
490 | 17129 | 42E9 | 04 | read
491 | 17130 | 42EA | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
492 | 17131 | 42EB | 04 | read
493 | 17132 | 42EC | 04 | read | last 8 month spike | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
494 | 17133 | 42ED | 04 | read
495 | 17134 | 42EE | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
496 | 17135 | 42EF | 04 | read
497 | 17136 | 42F0 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
498 | 17137 | 42F1 | 04 | read
499 | 17138 | 42F2 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
500 | 17139 | 42F3 | 04 | read
501 | 17140 | 42F4 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
502 | 17141 | 42F5 | 04 | read
503 | 17142 | 42F6 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
504 | 17143 | 42F7 | 04 | read
505 | 17144 | 42F8 | 04 | read | last 8 month peak | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
506 | 17145 | 42F9 | 04 | read
507 | 17146 | 42FA | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
508 | 17147 | 42FB | 04 | read
509 | 17148 | 42FC | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
510 | 17149 | 42FD | 04 | read
511 | 17150 | 42FE | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
512 | 17151 | 42FF | 04 | read
513 | 17152 | 4300 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
514 | 17153 | 4301 | 04 | read
515 | 17154 | 4302 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
516 | 17155 | 4303 | 04 | read
517 | 17156 | 4304 | 04 | read | last 8 month flat | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
518 | 17157 | 4305 | 04 | read
519 | 17158 | 4306 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
520 | 17159 | 4307 | 04 | read
521 | 17160 | 4308 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
522 | 17161 | 4309 | 04 | read
523 | 17162 | 430A | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
524 | 17163 | 430B | 04 | read
525 | 17164 | 430C | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
526 | 17165 | 430D | 04 | read
527 | 17166 | 430E | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
528 | 17167 | 430F | 04 | read
529 | 17168 | 4310 | 04 | read | last 8 month valley | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
530 | 17169 | 4311 | 04 | read
531 | 17170 | 4312 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
532 | 17171 | 4313 | 04 | read
533 | 17172 | 4314 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
534 | 17173 | 4315 | 04 | read
535 | 17174 | 4316 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
536 | 17175 | 4317 | 04 | read
537 | 17176 | 4318 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
538 | 17177 | 4319 | 04 | read
539 | 17178 | 431A | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
540 | 17179 | 431B | 04 | read
541 | 17180 | 431C | 04 | read | last 9 month total | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
542 | 17181 | 431D | 04 | read
543 | 17182 | 431E | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
544 | 17183 | 431F | 04 | read
545 | 17184 | 4320 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
546 | 17185 | 4321 | 04 | read
547 | 17186 | 4322 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
548 | 17187 | 4323 | 04 | read
549 | 17188 | 4324 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
550 | 17189 | 4325 | 04 | read
551 | 17190 | 4326 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
552 | 17191 | 4327 | 04 | read
553 | 17192 | 4328 | 04 | read | last 9 month spike | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
554 | 17193 | 4329 | 04 | read
555 | 17194 | 432A | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
556 | 17195 | 432B | 04 | read
557 | 17196 | 432C | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
558 | 17197 | 432D | 04 | read
559 | 17198 | 432E | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
560 | 17199 | 432F | 04 | read
561 | 17200 | 4330 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
562 | 17201 | 4331 | 04 | read
563 | 17202 | 4332 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
564 | 17203 | 4333 | 04 | read
565 | 17204 | 4334 | 04 | read | last 9 month peak | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
566 | 17205 | 4335 | 04 | read
567 | 17206 | 4336 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
568 | 17207 | 4337 | 04 | read
569 | 17208 | 4338 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
570 | 17209 | 4339 | 04 | read
571 | 17210 | 433A | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
572 | 17211 | 433B | 04 | read
573 | 17212 | 433C | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
574 | 17213 | 433D | 04 | read
575 | 17214 | 433E | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
576 | 17215 | 433F | 04 | read
577 | 17216 | 4340 | 04 | read | last 9 month flat | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
578 | 17217 | 4341 | 04 | read
579 | 17218 | 4342 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
580 | 17219 | 4343 | 04 | read
581 | 17220 | 4344 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
582 | 17221 | 4345 | 04 | read
583 | 17222 | 4346 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
584 | 17223 | 4347 | 04 | read
585 | 17224 | 4348 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
586 | 17225 | 4349 | 04 | read
587 | 17226 | 434A | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
588 | 17227 | 434B | 04 | read
589 | 17228 | 434C | 04 | read | last 9 month valley | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
590 | 17229 | 434D | 04 | read
591 | 17230 | 434E | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
592 | 17231 | 434F | 04 | read
593 | 17232 | 4350 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
594 | 17233 | 4351 | 04 | read
595 | 17234 | 4352 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
596 | 17235 | 4353 | 04 | read
597 | 17236 | 4354 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
598 | 17237 | 4355 | 04 | read
599 | 17238 | 4356 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
600 | 17239 | 4357 | 04 | read
601 | 17240 | 4358 | 04 | read | last 10 month total | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
602 | 17241 | 4359 | 04 | read
603 | 17242 | 435A | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
604 | 17243 | 435B | 04 | read
605 | 17244 | 435C | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
606 | 17245 | 435D | 04 | read
607 | 17246 | 435E | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
608 | 17247 | 435F | 04 | read
609 | 17248 | 4360 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
610 | 17249 | 4361 | 04 | read
611 | 17250 | 4362 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
612 | 17251 | 4363 | 04 | read
613 | 17252 | 4364 | 04 | read | last 10 month spike | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
614 | 17253 | 4365 | 04 | read
615 | 17254 | 4366 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
616 | 17255 | 4367 | 04 | read
617 | 17256 | 4368 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
618 | 17257 | 4369 | 04 | read
619 | 17258 | 436A | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
620 | 17259 | 436B | 04 | read
621 | 17260 | 436C | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
622 | 17261 | 436D | 04 | read
623 | 17262 | 436E | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
624 | 17263 | 436F | 04 | read
625 | 17264 | 4370 | 04 | read | last 10 month peak | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
626 | 17265 | 4371 | 04 | read
627 | 17266 | 4372 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
628 | 17267 | 4373 | 04 | read
629 | 17268 | 4374 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
630 | 17269 | 4375 | 04 | read
631 | 17270 | 4376 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
632 | 17271 | 4377 | 04 | read
633 | 17272 | 4378 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
634 | 17273 | 4379 | 04 | read
635 | 17274 | 437A | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
636 | 17275 | 437B | 04 | read
637 | 17276 | 437C | 04 | read | last 10 month flat | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
638 | 17277 | 437D | 04 | read
639 | 17278 | 437E | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
640 | 17279 | 437F | 04 | read
641 | 17280 | 4380 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
642 | 17281 | 4381 | 04 | read
643 | 17282 | 4382 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
644 | 17283 | 4383 | 04 | read
645 | 17284 | 4384 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
646 | 17285 | 4385 | 04 | read
647 | 17286 | 4386 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
648 | 17287 | 4387 | 04 | read
649 | 17288 | 4388 | 04 | read | last 10 month valley | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
650 | 17289 | 4389 | 04 | read
651 | 17290 | 438A | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
652 | 17291 | 438B | 04 | read
653 | 17292 | 438C | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
654 | 17293 | 438D | 04 | read
655 | 17294 | 438E | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
656 | 17295 | 438F | 04 | read
657 | 17296 | 4390 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
658 | 17297 | 4391 | 04 | read
659 | 17298 | 4392 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
660 | 17299 | 4393 | 04 | read
661 | 17300 | 4394 | 04 | read | last 11 month total | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
662 | 17301 | 4395 | 04 | read
663 | 17302 | 4396 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
664 | 17303 | 4397 | 04 | read
665 | 17304 | 4398 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
666 | 17305 | 4399 | 04 | read
667 | 17306 | 439A | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
668 | 17307 | 439B | 04 | read
669 | 17308 | 439C | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
670 | 17309 | 439D | 04 | read
671 | 17310 | 439E | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
672 | 17311 | 439F | 04 | read
673 | 17312 | 43A0 | 04 | read | last 11 month spike | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
674 | 17313 | 43A1 | 04 | read
675 | 17314 | 43A2 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
676 | 17315 | 43A3 | 04 | read
677 | 17316 | 43A4 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
678 | 17317 | 43A5 | 04 | read
679 | 17318 | 43A6 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
680 | 17319 | 43A7 | 04 | read
681 | 17320 | 43A8 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
682 | 17321 | 43A9 | 04 | read
683 | 17322 | 43AA | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
684 | 17323 | 43AB | 04 | read
685 | 17324 | 43AC | 04 | read | last 11 month peak | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
686 | 17325 | 43AD | 04 | read
687 | 17326 | 43AE | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
688 | 17327 | 43AF | 04 | read
689 | 17328 | 43B0 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
690 | 17329 | 43B1 | 04 | read
691 | 17330 | 43B2 | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
692 | 17331 | 43B3 | 04 | read
693 | 17332 | 43B4 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
694 | 17333 | 43B5 | 04 | read
695 | 17334 | 43B6 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
696 | 17335 | 43B7 | 04 | read
697 | 17336 | 43B8 | 04 | read | last 11 month flat | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
698 | 17337 | 43B9 | 04 | read
699 | 17338 | 43BA | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
700 | 17339 | 43BB | 04 | read
701 | 17340 | 43BC | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
702 | 17341 | 43BD | 04 | read
703 | 17342 | 43BE | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
704 | 17343 | 43BF | 04 | read
705 | 17344 | 43C0 | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
706 | 17345 | 43C1 | 04 | read
707 | 17346 | 43C2 | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
708 | 17347 | 43C3 | 04 | read
709 | 17348 | 43C4 | 04 | read | last 11 month valley | total active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
710 | 17349 | 43C5 | 04 | read
711 | 17350 | 43C6 | 04 | read |  | forward active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
712 | 17351 | 43C7 | 04 | read
713 | 17352 | 43C8 | 04 | read |  | reversing active energy | unsigned 32 bit | 0 | 0～999999999 | kWh | amplify 10 times
714 | 17353 | 43C9 | 04 | read
715 | 17354 | 43CA | 04 | read |  | total reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
716 | 17355 | 43CB | 04 | read
717 | 17356 | 43CC | 04 | read |  | forward reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
718 | 17357 | 43CD | 04 | read
719 | 17358 | 43CE | 04 | read |  | reversing reactive energy | unsigned 32 bit | 0 | 0～999999999 | kvarh | amplify 10 times
720 | 17359 | 43CF | 04 | read

## 8XXX Zone SOE Record
SOE Event Record
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range | Remark
1 | 32768 | 8000 | 04 | read | 1 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-99 | Group：0 member： 0：no event 1：DI1 off 2：DI1 on 3：DI2 off 4：DI2 on
2 | 32769 | 8001 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-12
3 | 32770 | 8002 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-23
4 | 32771 | 8003 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-59
5 | 32772 | 8004 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1000
6 | 32773 | 8005 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
7 | 32774 | 8006
8 | 32775 | 8007 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
9 | 32776 | 8008
10 | 32777 | 8009 | 04 | read | 2 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-100
11 | 32778 | 800A | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-13
12 | 32779 | 800B | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-24
13 | 32780 | 800C | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-60
14 | 32781 | 800D | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1001
15 | 32782 | 800E | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
16 | 32783 | 800F
17 | 32784 | 8010 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
18 | 32785 | 8011
19 | 32786 | 8012 | 04 | read | 3 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-100
20 | 32787 | 8013 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-13
21 | 32788 | 8014 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-24
22 | 32789 | 8015 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-60
23 | 32790 | 8016 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1001
24 | 32791 | 8017 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
25 | 32792 | 8018
26 | 32793 | 8019 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
27 | 32794 | 801A
28 | 32795 | 801B | 04 | read | 4 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-101
29 | 32796 | 801C | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-14
30 | 32797 | 801D | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-25
31 | 32798 | 801E | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-61
32 | 32799 | 801F | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1002
33 | 32800 | 8020 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
34 | 32801 | 8021
35 | 32802 | 8022 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
36 | 32803 | 8023
37 | 32804 | 8024 | 04 | read | 5 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-102
38 | 32805 | 8025 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-15
39 | 32806 | 8026 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-26
40 | 32807 | 8027 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-62
41 | 32808 | 8028 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1003
42 | 32809 | 8029 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
43 | 32810 | 802A
44 | 32811 | 802B | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
45 | 32812 | 802C
46 | 32813 | 802D | 04 | read | 6 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-102
47 | 32814 | 802E | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-15
48 | 32815 | 802F | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-26
49 | 32816 | 8030 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-62
50 | 32817 | 8031 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1003
51 | 32818 | 8032 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
52 | 32819 | 8033
53 | 32820 | 8034 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
54 | 32821 | 8035
55 | 32822 | 8036 | 04 | read | 7 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-103
56 | 32823 | 8037 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-16
57 | 32824 | 8038 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-27
58 | 32825 | 8039 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-63
59 | 32826 | 803A | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1004
60 | 32827 | 803B | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
61 | 32828 | 803C
62 | 32829 | 803D | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
63 | 32830 | 803E
64 | 32831 | 803F | 04 | read | 8 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-104
65 | 32832 | 8040 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-17
66 | 32833 | 8041 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-28
67 | 32834 | 8042 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-64
68 | 32835 | 8043 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1005
69 | 32836 | 8044 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
70 | 32837 | 8045
71 | 32838 | 8046 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
72 | 32839 | 8047
73 | 32840 | 8048 | 04 | read | 9 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-105 | Group：1 Member： 0：no event 1：DO1 off 2：DO1 on 3：DO2 off 4：DO2 on
74 | 32841 | 8049 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-18
75 | 32842 | 804A | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-29
76 | 32843 | 804B | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-65
77 | 32844 | 804C | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1006
78 | 32845 | 804D | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
79 | 32846 | 804E
80 | 32847 | 804F | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
81 | 32848 | 8050
82 | 32849 | 8051 | 04 | read | 10 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-106
83 | 32850 | 8052 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-19
84 | 32851 | 8053 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-30
85 | 32852 | 8054 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-66
86 | 32853 | 8055 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1007
87 | 32854 | 8056 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
88 | 32855 | 8057
89 | 32856 | 8058 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
90 | 32857 | 8059
91 | 32858 | 805A | 04 | read | 11 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-107
92 | 32859 | 805B | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-20
93 | 32860 | 805C | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-31
94 | 32861 | 805D | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-67
95 | 32862 | 805E | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1008
96 | 32863 | 805F | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
97 | 32864 | 8060
98 | 32865 | 8061 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
99 | 32866 | 8062
100 | 32867 | 8063 | 04 | read | 12 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-108
101 | 32868 | 8064 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-21
102 | 32869 | 8065 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-32
103 | 32870 | 8066 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-68
104 | 32871 | 8067 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1009
105 | 32872 | 8068 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
106 | 32873 | 8069
107 | 32874 | 806A | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
108 | 32875 | 806B
109 | 32876 | 806C | 04 | read | 13 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
110 | 32877 | 806D | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
111 | 32878 | 806E | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
112 | 32879 | 806F | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
113 | 32880 | 8070 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
114 | 32881 | 8071 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
115 | 32882 | 8072
116 | 32883 | 8073 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
117 | 32884 | 8074
118 | 32885 | 8075 | 04 | read | 14 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-108
119 | 32886 | 8076 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-21
120 | 32887 | 8077 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-32
121 | 32888 | 8078 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-68
122 | 32889 | 8079 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1009
123 | 32890 | 807A | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
124 | 32891 | 807B
125 | 32892 | 807C | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
126 | 32893 | 807D
127 | 32894 | 807E | 04 | read | 15 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
128 | 32895 | 807F | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
129 | 32896 | 8080 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
130 | 32897 | 8081 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
131 | 32898 | 8082 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
132 | 32899 | 8083 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
133 | 32900 | 8084
134 | 32901 | 8085 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
135 | 32902 | 8086
136 | 32903 | 8087 | 04 | read | 16 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
137 | 32904 | 8088 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
138 | 32905 | 8089 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
139 | 32906 | 808A | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
140 | 32907 | 808B | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
141 | 32908 | 808C | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
142 | 32909 | 808D
143 | 32910 | 808E | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
144 | 32911 | 808F
145 | 32912 | 8090 | 04 | read | 17 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-108 | Group：2 Member： 0：no event 1：phase A volatge upper limit 2：phase A volatge limit 3：phase A voltage lower limit 4：phase B volatge upper limit 5：phase B volatge limit 6：phase B voltage lower limit 7：phase C volatge upper limit 8：phase C volatge limit 9：phase C voltage lower limit 10：phase A current upper limit 11：phase A current limit 12：phase B current upper limit 13：phase B current limit 14: phase C current upper limit 15：phase C current limit 16: leakage current upper current 17：leakage current limit 18：T1 temperature upper limit 19：T1 temperature limit 20：T2 temperature upper limit 21：T2 temperature limit 22：T3 temperature upper limit 23：T3 temperature limit 24：T4 temperature upper limit 25：T4 temperature limit
146 | 32913 | 8091 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-21
147 | 32914 | 8092 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-32
148 | 32915 | 8093 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-68
149 | 32916 | 8094 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1009
150 | 32917 | 8095 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
151 | 32918 | 8096
152 | 32919 | 8097 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
153 | 32920 | 8098
154 | 32921 | 8099 | 04 | read | 18 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
155 | 32922 | 809A | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
156 | 32923 | 809B | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
157 | 32924 | 809C | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
158 | 32925 | 809D | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
159 | 32926 | 809E | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
160 | 32927 | 809F
161 | 32928 | 80A0 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
162 | 32929 | 80A1
163 | 32930 | 80A2 | 04 | read | 19 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
164 | 32931 | 80A3 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
165 | 32932 | 80A4 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
166 | 32933 | 80A5 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
167 | 32934 | 80A6 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
168 | 32935 | 80A7 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
169 | 32936 | 80A8
170 | 32937 | 80A9 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
171 | 32938 | 80AA
172 | 32939 | 80AB | 04 | read | 20 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
173 | 32940 | 80AC | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
174 | 32941 | 80AD | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
175 | 32942 | 80AE | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
176 | 32943 | 80AF | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
177 | 32944 | 80B0 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
178 | 32945 | 80B1
179 | 32946 | 80B2 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
180 | 32947 | 80B3
181 | 32948 | 80B4 | 04 | read | 21 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
182 | 32949 | 80B5 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
183 | 32950 | 80B6 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
184 | 32951 | 80B7 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
185 | 32952 | 80B8 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
186 | 32953 | 80B9 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
187 | 32954 | 80BA
188 | 32955 | 80BB | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
189 | 32956 | 80BC
190 | 32957 | 80BD | 04 | read | 22 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
191 | 32958 | 80BE | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
192 | 32959 | 80BF | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
193 | 32960 | 80C0 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
194 | 32961 | 80C1 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
195 | 32962 | 80C2 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
196 | 32963 | 80C3
197 | 32964 | 80C4 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
198 | 32965 | 80C5
199 | 32966 | 80C6 | 04 | read | 23 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-108
200 | 32967 | 80C7 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-21
201 | 32968 | 80C8 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-32
202 | 32969 | 80C9 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-68
203 | 32970 | 80CA | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1009
204 | 32971 | 80CB | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
205 | 32972 | 80CC
206 | 32973 | 80CD | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
207 | 32974 | 80CE
208 | 32975 | 80CF | 04 | read | 24 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
209 | 32976 | 80D0 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
210 | 32977 | 80D1 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
211 | 32978 | 80D2 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
212 | 32979 | 80D3 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
213 | 32980 | 80D4 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
214 | 32981 | 80D5
215 | 32982 | 80D6 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
216 | 32983 | 80D7
217 | 32984 | 80D8 | 04 | read | 25 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
218 | 32985 | 80D9 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
219 | 32986 | 80DA | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
220 | 32987 | 80DB | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
221 | 32988 | 80DC | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
222 | 32989 | 80DD | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
223 | 32990 | 80DE
224 | 32991 | 80DF | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
225 | 32992 | 80E0
226 | 32993 | 80E1 | 04 | read | 26 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
227 | 32994 | 80E2 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
228 | 32995 | 80E3 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
229 | 32996 | 80E4 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
230 | 32997 | 80E5 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
231 | 32998 | 80E6 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
232 | 32999 | 80E7
233 | 33000 | 80E8 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
234 | 33001 | 80E9
235 | 33002 | 80EA | 04 | read | 27 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
236 | 33003 | 80EB | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
237 | 33004 | 80EC | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
238 | 33005 | 80ED | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
239 | 33006 | 80EE | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
240 | 33007 | 80EF | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
241 | 33008 | 80F0
242 | 33009 | 80F1 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
243 | 33010 | 80F2
244 | 33011 | 80F3 | 04 | read | 28 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
245 | 33012 | 80F4 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
246 | 33013 | 80F5 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
247 | 33014 | 80F6 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
248 | 33015 | 80F7 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
249 | 33016 | 80F8 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
250 | 33017 | 80F9
251 | 33018 | 80FA | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
252 | 33019 | 80FB
253 | 33020 | 80FC | 04 | read | 29 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
254 | 33021 | 80FD | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
255 | 33022 | 80FE | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
256 | 33023 | 80FF | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
257 | 33024 | 8100 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
258 | 33025 | 8101 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
259 | 33026 | 8102
260 | 33027 | 8103 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
261 | 33028 | 8104
262 | 33029 | 8105 | 04 | read | 30 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
263 | 33030 | 8106 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
264 | 33031 | 8107 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
265 | 33032 | 8108 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
266 | 33033 | 8109 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
267 | 33034 | 810A | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
268 | 33035 | 810B
269 | 33036 | 810C | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
270 | 33037 | 810D
271 | 33038 | 810E | 04 | read | 31 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
272 | 33039 | 810F | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
273 | 33040 | 8110 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
274 | 33041 | 8111 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
275 | 33042 | 8112 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
276 | 33043 | 8113 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
277 | 33044 | 8114
278 | 33045 | 8115 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
279 | 33046 | 8116
280 | 33047 | 8117 | 04 | read | 32 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
281 | 33048 | 8118 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
282 | 33049 | 8119 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
283 | 33050 | 811A | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
284 | 33051 | 811B | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
285 | 33052 | 811C | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
286 | 33053 | 811D
287 | 33054 | 811E | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
288 | 33055 | 811F
289 | 33056 | 8120 | 04 | read | 33 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
290 | 33057 | 8121 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
291 | 33058 | 8122 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
292 | 33059 | 8123 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
293 | 33060 | 8124 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
294 | 33061 | 8125 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
295 | 33062 | 8126
296 | 33063 | 8127 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
297 | 33064 | 8128
298 | 33065 | 8129 | 04 | read | 34 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
299 | 33066 | 812A | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
300 | 33067 | 812B | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
301 | 33068 | 812C | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
302 | 33069 | 812D | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
303 | 33070 | 812E | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
304 | 33071 | 812F
305 | 33072 | 8130 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
306 | 33073 | 8131
307 | 33074 | 8132 | 04 | read | 35 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-108
308 | 33075 | 8133 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-21
309 | 33076 | 8134 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-32
310 | 33077 | 8135 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-68
311 | 33078 | 8136 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1009
312 | 33079 | 8137 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
313 | 33080 | 8138
314 | 33081 | 8139 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
315 | 33082 | 813A
316 | 33083 | 813B | 04 | read | 36 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
317 | 33084 | 813C | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
318 | 33085 | 813D | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
319 | 33086 | 813E | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
320 | 33087 | 813F | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
321 | 33088 | 8140 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
322 | 33089 | 8141
323 | 33090 | 8142 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
324 | 33091 | 8143
325 | 33092 | 8144 | 04 | read | 37 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
326 | 33093 | 8145 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
327 | 33094 | 8146 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
328 | 33095 | 8147 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
329 | 33096 | 8148 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
330 | 33097 | 8149 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
331 | 33098 | 814A
332 | 33099 | 814B | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
333 | 33100 | 814C
334 | 33101 | 814D | 04 | read | 38 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
335 | 33102 | 814E | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
336 | 33103 | 814F | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
337 | 33104 | 8150 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
338 | 33105 | 8151 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
339 | 33106 | 8152 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
340 | 33107 | 8153
341 | 33108 | 8154 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
342 | 33109 | 8155
343 | 33110 | 8156 | 04 | read | 39 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
344 | 33111 | 8157 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
345 | 33112 | 8158 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
346 | 33113 | 8159 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
347 | 33114 | 815A | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
348 | 33115 | 815B | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
349 | 33116 | 815C
350 | 33117 | 815D | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
351 | 33118 | 815E
352 | 33119 | 815F | 04 | read | 40 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
353 | 33120 | 8160 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
354 | 33121 | 8161 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
355 | 33122 | 8162 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
356 | 33123 | 8163 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
357 | 33124 | 8164 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
358 | 33125 | 8165
359 | 33126 | 8166 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
360 | 33127 | 8167
361 | 33128 | 8168 | 04 | read | 41 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
362 | 33129 | 8169 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
363 | 33130 | 816A | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
364 | 33131 | 816B | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
365 | 33132 | 816C | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
366 | 33133 | 816D | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
367 | 33134 | 816E
368 | 33135 | 816F | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
369 | 33136 | 8170
370 | 33137 | 8171 | 04 | read | 42 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
371 | 33138 | 8172 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
372 | 33139 | 8173 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
373 | 33140 | 8174 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
374 | 33141 | 8175 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
375 | 33142 | 8176 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
376 | 33143 | 8177
377 | 33144 | 8178 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
378 | 33145 | 8179
379 | 33146 | 817A | 04 | read | 43 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
380 | 33147 | 817B | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
381 | 33148 | 817C | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
382 | 33149 | 817D | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
383 | 33150 | 817E | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
384 | 33151 | 817F | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
385 | 33152 | 8180
386 | 33153 | 8181 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
387 | 33154 | 8182
388 | 33155 | 8183 | 04 | read | 44 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
389 | 33156 | 8184 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
390 | 33157 | 8185 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
391 | 33158 | 8186 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
392 | 33159 | 8187 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
393 | 33160 | 8188 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
394 | 33161 | 8189
395 | 33162 | 818A | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
396 | 33163 | 818B
397 | 33164 | 818C | 04 | read | 45 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
398 | 33165 | 818D | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
399 | 33166 | 818E | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
400 | 33167 | 818F | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
401 | 33168 | 8190 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
402 | 33169 | 8191 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
403 | 33170 | 8192
404 | 33171 | 8193 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
405 | 33172 | 8194
406 | 33173 | 8195 | 04 | read | 46 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
407 | 33174 | 8196 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
408 | 33175 | 8197 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
409 | 33176 | 8198 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
410 | 33177 | 8199 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
411 | 33178 | 819A | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
412 | 33179 | 819B
413 | 33180 | 819C | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
414 | 33181 | 819D
415 | 33182 | 819E | 04 | read | 47 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
416 | 33183 | 819F | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
417 | 33184 | 81A0 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
418 | 33185 | 81A1 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
419 | 33186 | 81A2 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
420 | 33187 | 81A3 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
421 | 33188 | 81A4
422 | 33189 | 81A5 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
423 | 33190 | 81A6
424 | 33191 | 81A7 | 04 | read | 48 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
425 | 33192 | 81A8 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
426 | 33193 | 81A9 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
427 | 33194 | 81AA | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
428 | 33195 | 81AB | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
429 | 33196 | 81AC | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
430 | 33197 | 81AD
431 | 33198 | 81AE | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
432 | 33199 | 81AF
433 | 33200 | 81B0 | 04 | read | 49 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
434 | 33201 | 81B1 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
435 | 33202 | 81B2 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
436 | 33203 | 81B3 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
437 | 33204 | 81B4 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
438 | 33205 | 81B5 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
439 | 33206 | 81B6
440 | 33207 | 81B7 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
441 | 33208 | 81B8
442 | 33209 | 81B9 | 04 | read | 50 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
443 | 33210 | 81BA | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
444 | 33211 | 81BB | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
445 | 33212 | 81BC | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
446 | 33213 | 81BD | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
447 | 33214 | 81BE | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
448 | 33215 | 81BF
449 | 33216 | 81C0 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
450 | 33217 | 81C1
451 | 33218 | 81C2 | 04 | read | 51 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
452 | 33219 | 81C3 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
453 | 33220 | 81C4 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
454 | 33221 | 81C5 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
455 | 33222 | 81C6 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
456 | 33223 | 81C7 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
457 | 33224 | 81C8
458 | 33225 | 81C9 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
459 | 33226 | 81CA
460 | 33227 | 81CB | 04 | read | 52 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
461 | 33228 | 81CC | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
462 | 33229 | 81CD | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
463 | 33230 | 81CE | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
464 | 33231 | 81CF | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
465 | 33232 | 81D0 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
466 | 33233 | 81D1
467 | 33234 | 81D2 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
468 | 33235 | 81D3
469 | 33236 | 81D4 | 04 | read | 53 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
470 | 33237 | 81D5 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
471 | 33238 | 81D6 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
472 | 33239 | 81D7 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
473 | 33240 | 81D8 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
474 | 33241 | 81D9 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
475 | 33242 | 81DA
476 | 33243 | 81DB | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
477 | 33244 | 81DC
478 | 33245 | 81DD | 04 | read | 54 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
479 | 33246 | 81DE | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
480 | 33247 | 81DF | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
481 | 33248 | 81E0 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
482 | 33249 | 81E1 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
483 | 33250 | 81E2 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
484 | 33251 | 81E3
485 | 33252 | 81E4 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
486 | 33253 | 81E5
487 | 33254 | 81E6 | 04 | read | 55 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
488 | 33255 | 81E7 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
489 | 33256 | 81E8 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
490 | 33257 | 81E9 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
491 | 33258 | 81EA | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
492 | 33259 | 81EB | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
493 | 33260 | 81EC
494 | 33261 | 81ED | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
495 | 33262 | 81EE
496 | 33263 | 81EF | 04 | read | 56 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
497 | 33264 | 81F0 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
498 | 33265 | 81F1 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
499 | 33266 | 81F2 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
500 | 33267 | 81F3 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
501 | 33268 | 81F4 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
502 | 33269 | 81F5
503 | 33270 | 81F6 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
504 | 33271 | 81F7
505 | 33272 | 81F8 | 04 | read | 57 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
506 | 33273 | 81F9 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
507 | 33274 | 81FA | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
508 | 33275 | 81FB | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
509 | 33276 | 81FC | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
510 | 33277 | 81FD | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
511 | 33278 | 81FE
512 | 33279 | 81FF | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
513 | 33280 | 8200
514 | 33281 | 8201 | 04 | read | 58 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-113
515 | 33282 | 8202 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-26
516 | 33283 | 8203 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-37
517 | 33284 | 8204 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-73
518 | 33285 | 8205 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1014
519 | 33286 | 8206 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
520 | 33287 | 8207
521 | 33288 | 8208 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
522 | 33289 | 8209
523 | 33290 | 820A | 04 | read | 59 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-108
524 | 33291 | 820B | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-21
525 | 33292 | 820C | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-32
526 | 33293 | 820D | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-68
527 | 33294 | 820E | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1009
528 | 33295 | 820F | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
529 | 33296 | 8210
530 | 33297 | 8211 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
531 | 33298 | 8212
532 | 33299 | 8213 | 04 | read | 60 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
533 | 33300 | 8214 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
534 | 33301 | 8215 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
535 | 33302 | 8216 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
536 | 33303 | 8217 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
537 | 33304 | 8218 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
538 | 33305 | 8219
539 | 33306 | 821A | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
540 | 33307 | 821B
541 | 33308 | 821C | 04 | read | 61 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
542 | 33309 | 821D | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
543 | 33310 | 821E | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
544 | 33311 | 821F | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
545 | 33312 | 8220 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
546 | 33313 | 8221 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
547 | 33314 | 8222
548 | 33315 | 8223 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
549 | 33316 | 8224
550 | 33317 | 8225 | 04 | read | 62 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
551 | 33318 | 8226 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
552 | 33319 | 8227 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
553 | 33320 | 8228 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
554 | 33321 | 8229 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
555 | 33322 | 822A | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
556 | 33323 | 822B
557 | 33324 | 822C | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
558 | 33325 | 822D
559 | 33326 | 822E | 04 | read | 63 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
560 | 33327 | 822F | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
561 | 33328 | 8230 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
562 | 33329 | 8231 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
563 | 33330 | 8232 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
564 | 33331 | 8233 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
565 | 33332 | 8234
566 | 33333 | 8235 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
567 | 33334 | 8236
568 | 33335 | 8237 | 04 | read | 64 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
569 | 33336 | 8238 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
570 | 33337 | 8239 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
571 | 33338 | 823A | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
572 | 33339 | 823B | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
573 | 33340 | 823C | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
574 | 33341 | 823D
575 | 33342 | 823E | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
576 | 33343 | 823F
577 | 33344 | 8240 | 04 | read | 65 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
578 | 33345 | 8241 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
579 | 33346 | 8242 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
580 | 33347 | 8243 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
581 | 33348 | 8244 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
582 | 33349 | 8245 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
583 | 33350 | 8246
584 | 33351 | 8247 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
585 | 33352 | 8248
586 | 33353 | 8249 | 04 | read | 66 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
587 | 33354 | 824A | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
588 | 33355 | 824B | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
589 | 33356 | 824C | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
590 | 33357 | 824D | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
591 | 33358 | 824E | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
592 | 33359 | 824F
593 | 33360 | 8250 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
594 | 33361 | 8251
595 | 33362 | 8252 | 04 | read | 67 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
596 | 33363 | 8253 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
597 | 33364 | 8254 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
598 | 33365 | 8255 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
599 | 33366 | 8256 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
600 | 33367 | 8257 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
601 | 33368 | 8258
602 | 33369 | 8259 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
603 | 33370 | 825A
604 | 33371 | 825B | 04 | read | 68 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
605 | 33372 | 825C | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
606 | 33373 | 825D | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
607 | 33374 | 825E | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
608 | 33375 | 825F | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
609 | 33376 | 8260 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
610 | 33377 | 8261
611 | 33378 | 8262 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
612 | 33379 | 8263
613 | 33380 | 8264 | 04 | read | 69 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
614 | 33381 | 8265 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
615 | 33382 | 8266 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
616 | 33383 | 8267 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
617 | 33384 | 8268 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
618 | 33385 | 8269 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
619 | 33386 | 826A
620 | 33387 | 826B | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
621 | 33388 | 826C
622 | 33389 | 826D | 04 | read | 70 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
623 | 33390 | 826E | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
624 | 33391 | 826F | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
625 | 33392 | 8270 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
626 | 33393 | 8271 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
627 | 33394 | 8272 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
628 | 33395 | 8273
629 | 33396 | 8274 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
630 | 33397 | 8275
631 | 33398 | 8276 | 04 | read | 71 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
632 | 33399 | 8277 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
633 | 33400 | 8278 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
634 | 33401 | 8279 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
635 | 33402 | 827A | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
636 | 33403 | 827B | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
637 | 33404 | 827C
638 | 33405 | 827D | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
639 | 33406 | 827E
640 | 33407 | 827F | 04 | read | 72 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
641 | 33408 | 8280 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
642 | 33409 | 8281 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
643 | 33410 | 8282 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
644 | 33411 | 8283 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
645 | 33412 | 8284 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
646 | 33413 | 8285
647 | 33414 | 8286 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
648 | 33415 | 8287
649 | 33416 | 8288 | 04 | read | 73 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
650 | 33417 | 8289 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
651 | 33418 | 828A | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
652 | 33419 | 828B | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
653 | 33420 | 828C | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
654 | 33421 | 828D | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
655 | 33422 | 828E
656 | 33423 | 828F | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
657 | 33424 | 8290
658 | 33425 | 8291 | 04 | read | 74 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
659 | 33426 | 8292 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
660 | 33427 | 8293 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
661 | 33428 | 8294 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
662 | 33429 | 8295 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
663 | 33430 | 8296 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
664 | 33431 | 8297
665 | 33432 | 8298 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
666 | 33433 | 8299
667 | 33434 | 829A | 04 | read | 75 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
668 | 33435 | 829B | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
669 | 33436 | 829C | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
670 | 33437 | 829D | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
671 | 33438 | 829E | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
672 | 33439 | 829F | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
673 | 33440 | 82A0
674 | 33441 | 82A1 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
675 | 33442 | 82A2
676 | 33443 | 82A3 | 04 | read | 76 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
677 | 33444 | 82A4 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
678 | 33445 | 82A5 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
679 | 33446 | 82A6 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
680 | 33447 | 82A7 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
681 | 33448 | 82A8 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
682 | 33449 | 82A9
683 | 33450 | 82AA | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
684 | 33451 | 82AB
685 | 33452 | 82AC | 04 | read | 77 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
686 | 33453 | 82AD | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
687 | 33454 | 82AE | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
688 | 33455 | 82AF | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
689 | 33456 | 82B0 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
690 | 33457 | 82B1 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
691 | 33458 | 82B2
692 | 33459 | 82B3 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
693 | 33460 | 82B4
694 | 33461 | 82B5 | 04 | read | 78 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
695 | 33462 | 82B6 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
696 | 33463 | 82B7 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
697 | 33464 | 82B8 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
698 | 33465 | 82B9 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
699 | 33466 | 82BA | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
700 | 33467 | 82BB
701 | 33468 | 82BC | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
702 | 33469 | 82BD
703 | 33470 | 82BE | 04 | read | 79 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
704 | 33471 | 82BF | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
705 | 33472 | 82C0 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
706 | 33473 | 82C1 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
707 | 33474 | 82C2 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
708 | 33475 | 82C3 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
709 | 33476 | 82C4
710 | 33477 | 82C5 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
711 | 33478 | 82C6
712 | 33479 | 82C7 | 04 | read | 80 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
713 | 33480 | 82C8 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
714 | 33481 | 82C9 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
715 | 33482 | 82CA | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
716 | 33483 | 82CB | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
717 | 33484 | 82CC | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
718 | 33485 | 82CD
719 | 33486 | 82CE | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
720 | 33487 | 82CF
721 | 33488 | 82D0 | 04 | read | 81 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112 | Group：3 Member： 0：no event 1：leakage current short circuit 2：leakage current breaker 3：T1 temperature short circuit 4：T1 temperature breaker 5：T2 temperature short circuit 6：T2 temperature breaker 7：T3 temperature short circuit 8：T3 temperature breaker 9：T4 temperature short circuit 10：T4 temperature breaker
722 | 33489 | 82D1 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
723 | 33490 | 82D2 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
724 | 33491 | 82D3 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
725 | 33492 | 82D4 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
726 | 33493 | 82D5 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
727 | 33494 | 82D6
728 | 33495 | 82D7 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
729 | 33496 | 82D8
730 | 33497 | 82D9 | 04 | read | 82 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-113
731 | 33498 | 82DA | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-26
732 | 33499 | 82DB | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-37
733 | 33500 | 82DC | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-73
734 | 33501 | 82DD | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1014
735 | 33502 | 82DE | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
736 | 33503 | 82DF
737 | 33504 | 82E0 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
738 | 33505 | 82E1
739 | 33506 | 82E2 | 04 | read | 83 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-109
740 | 33507 | 82E3 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-22
741 | 33508 | 82E4 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-33
742 | 33509 | 82E5 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-69
743 | 33510 | 82E6 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1010
744 | 33511 | 82E7 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
745 | 33512 | 82E8
746 | 33513 | 82E9 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
747 | 33514 | 82EA
748 | 33515 | 82EB | 04 | read | 84 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
749 | 33516 | 82EC | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
750 | 33517 | 82ED | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
751 | 33518 | 82EE | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
752 | 33519 | 82EF | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
753 | 33520 | 82F0 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
754 | 33521 | 82F1
755 | 33522 | 82F2 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
756 | 33523 | 82F3
757 | 33524 | 82F4 | 04 | read | 85 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
758 | 33525 | 82F5 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
759 | 33526 | 82F6 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
760 | 33527 | 82F7 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
761 | 33528 | 82F8 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
762 | 33529 | 82F9 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
763 | 33530 | 82FA
764 | 33531 | 82FB | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
765 | 33532 | 82FC
766 | 33533 | 82FD | 04 | read | 86 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
767 | 33534 | 82FE | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
768 | 33535 | 82FF | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
769 | 33536 | 8300 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
770 | 33537 | 8301 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
771 | 33538 | 8302 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
772 | 33539 | 8303
773 | 33540 | 8304 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
774 | 33541 | 8305
775 | 33542 | 8306 | 04 | read | 87 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
776 | 33543 | 8307 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
777 | 33544 | 8308 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
778 | 33545 | 8309 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
779 | 33546 | 830A | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
780 | 33547 | 830B | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
781 | 33548 | 830C
782 | 33549 | 830D | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
783 | 33550 | 830E
784 | 33551 | 830F | 04 | read | 88 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
785 | 33552 | 8310 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
786 | 33553 | 8311 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
787 | 33554 | 8312 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
788 | 33555 | 8313 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
789 | 33556 | 8314 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
790 | 33557 | 8315
791 | 33558 | 8316 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
792 | 33559 | 8317
793 | 33560 | 8318 | 04 | read | 89 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
794 | 33561 | 8319 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
795 | 33562 | 831A | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
796 | 33563 | 831B | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
797 | 33564 | 831C | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
798 | 33565 | 831D | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
799 | 33566 | 831E
800 | 33567 | 831F | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
801 | 33568 | 8320
802 | 33569 | 8321 | 04 | read | 90 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
803 | 33570 | 8322 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
804 | 33571 | 8323 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
805 | 33572 | 8324 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
806 | 33573 | 8325 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
807 | 33574 | 8326 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
808 | 33575 | 8327
809 | 33576 | 8328 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
810 | 33577 | 8329
811 | 33578 | 832A | 04 | read | 91 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
812 | 33579 | 832B | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
813 | 33580 | 832C | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
814 | 33581 | 832D | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
815 | 33582 | 832E | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
816 | 33583 | 832F | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
817 | 33584 | 8330
818 | 33585 | 8331 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
819 | 33586 | 8332
820 | 33587 | 8333 | 04 | read | 92 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
821 | 33588 | 8334 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
822 | 33589 | 8335 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
823 | 33590 | 8336 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
824 | 33591 | 8337 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
825 | 33592 | 8338 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
826 | 33593 | 8339
827 | 33594 | 833A | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
828 | 33595 | 833B
829 | 33596 | 833C | 04 | read | 93 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
830 | 33597 | 833D | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
831 | 33598 | 833E | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
832 | 33599 | 833F | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
833 | 33600 | 8340 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
834 | 33601 | 8341 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
835 | 33602 | 8342
836 | 33603 | 8343 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
837 | 33604 | 8344
838 | 33605 | 8345 | 04 | read | 94 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-113
839 | 33606 | 8346 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-26
840 | 33607 | 8347 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-37
841 | 33608 | 8348 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-73
842 | 33609 | 8349 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1014
843 | 33610 | 834A | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
844 | 33611 | 834B
845 | 33612 | 834C | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
846 | 33613 | 834D
847 | 33614 | 834E | 04 | read | 95 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-110
848 | 33615 | 834F | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-23
849 | 33616 | 8350 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-34
850 | 33617 | 8351 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-70
851 | 33618 | 8352 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1011
852 | 33619 | 8353 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
853 | 33620 | 8354
854 | 33621 | 8355 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
855 | 33622 | 8356
856 | 33623 | 8357 | 04 | read | 96 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
857 | 33624 | 8358 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
858 | 33625 | 8359 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
859 | 33626 | 835A | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
860 | 33627 | 835B | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
861 | 33628 | 835C | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
862 | 33629 | 835D
863 | 33630 | 835E | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
864 | 33631 | 835F
865 | 33632 | 8360 | 04 | read | 97 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
866 | 33633 | 8361 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
867 | 33634 | 8362 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
868 | 33635 | 8363 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
869 | 33636 | 8364 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
870 | 33637 | 8365 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
871 | 33638 | 8366
872 | 33639 | 8367 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
873 | 33640 | 8368
874 | 33641 | 8369 | 04 | read | 98 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
875 | 33642 | 836A | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
876 | 33643 | 836B | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
877 | 33644 | 836C | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
878 | 33645 | 836D | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
879 | 33646 | 836E | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
880 | 33647 | 836F
881 | 33648 | 8370 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
882 | 33649 | 8371
883 | 33650 | 8372 | 04 | read | 99 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
884 | 33651 | 8373 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
885 | 33652 | 8374 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
886 | 33653 | 8375 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
887 | 33654 | 8376 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
888 | 33655 | 8377 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
889 | 33656 | 8378
890 | 33657 | 8379 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
891 | 33658 | 837A
892 | 33659 | 837B | 04 | read | 100 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-113
893 | 33660 | 837C | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-26
894 | 33661 | 837D | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-37
895 | 33662 | 837E | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-73
896 | 33663 | 837F | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1014
897 | 33664 | 8380 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
898 | 33665 | 8381
899 | 33666 | 8382 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
900 | 33667 | 8383
901 | 33668 | 8384 | 04 | read | 101 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-111
902 | 33669 | 8385 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-24
903 | 33670 | 8386 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-35
904 | 33671 | 8387 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-71
905 | 33672 | 8388 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1012
906 | 33673 | 8389 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
907 | 33674 | 838A
908 | 33675 | 838B | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
909 | 33676 | 838C
910 | 33677 | 838D | 04 | read | 102 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
911 | 33678 | 838E | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
912 | 33679 | 838F | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
913 | 33680 | 8390 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
914 | 33681 | 8391 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
915 | 33682 | 8392 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
916 | 33683 | 8393
917 | 33684 | 8394 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
918 | 33685 | 8395
919 | 33686 | 8396 | 04 | read | 103 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-113
920 | 33687 | 8397 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-26
921 | 33688 | 8398 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-37
922 | 33689 | 8399 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-73
923 | 33690 | 839A | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1014
924 | 33691 | 839B | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
925 | 33692 | 839C
926 | 33693 | 839D | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
927 | 33694 | 839E
928 | 33695 | 839F | 04 | read | 104 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-112
929 | 33696 | 83A0 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-25
930 | 33697 | 83A1 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-36
931 | 33698 | 83A2 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-72
932 | 33699 | 83A3 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1013
933 | 33700 | 83A4 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
934 | 33701 | 83A5
935 | 33702 | 83A6 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
936 | 33703 | 83A7
937 | 33704 | 83A8 | 04 | read | 105 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-113
938 | 33705 | 83A9 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-26
939 | 33706 | 83AA | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-37
940 | 33707 | 83AB | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-73
941 | 33708 | 83AC | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1014
942 | 33709 | 83AD | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
943 | 33710 | 83AE
944 | 33711 | 83AF | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
945 | 33712 | 83B0
946 | 33713 | 83B1 | 04 | read | 106 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-114
947 | 33714 | 83B2 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-27
948 | 33715 | 83B3 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-38
949 | 33716 | 83B4 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-74
950 | 33717 | 83B5 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1015
951 | 33718 | 83B6 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
952 | 33719 | 83B7
953 | 33720 | 83B8 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
954 | 33721 | 83B9
955 | 33722 | 83BA | 04 | read | 107 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-115
956 | 33723 | 83BB | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-28
957 | 33724 | 83BC | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-39
958 | 33725 | 83BD | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-75
959 | 33726 | 83BE | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1016
960 | 33727 | 83BF | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
961 | 33728 | 83C0
962 | 33729 | 83C1 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
963 | 33730 | 83C2
964 | 33731 | 83C3 | 04 | read | 108 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-116
965 | 33732 | 83C4 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-29
966 | 33733 | 83C5 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-40
967 | 33734 | 83C6 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-76
968 | 33735 | 83C7 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1017
969 | 33736 | 83C8 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
970 | 33737 | 83C9
971 | 33738 | 83CA | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
972 | 33739 | 83CB
973 | 33740 | 83CC | 04 | read | 109 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-117
974 | 33741 | 83CD | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-30
975 | 33742 | 83CE | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-41
976 | 33743 | 83CF | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-77
977 | 33744 | 83D0 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1018
978 | 33745 | 83D1 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
979 | 33746 | 83D2
980 | 33747 | 83D3 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
981 | 33748 | 83D4
982 | 33749 | 83D5 | 04 | read | 110 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-118
983 | 33750 | 83D6 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-31
984 | 33751 | 83D7 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-42
985 | 33752 | 83D8 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-78
986 | 33753 | 83D9 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1019
987 | 33754 | 83DA | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
988 | 33755 | 83DB
989 | 33756 | 83DC | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
990 | 33757 | 83DD
991 | 33758 | 83DE | 04 | read | 111 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-119
992 | 33759 | 83DF | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-32
993 | 33760 | 83E0 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-43
994 | 33761 | 83E1 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-79
995 | 33762 | 83E2 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1020
996 | 33763 | 83E3 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
997 | 33764 | 83E4
998 | 33765 | 83E5 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
999 | 33766 | 83E6
1000 | 33767 | 83E7 | 04 | read | 112 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-120
1001 | 33768 | 83E8 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-33
1002 | 33769 | 83E9 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-44
1003 | 33770 | 83EA | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-80
1004 | 33771 | 83EB | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1021
1005 | 33772 | 83EC | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1006 | 33773 | 83ED
1007 | 33774 | 83EE | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1008 | 33775 | 83EF
1009 | 33776 | 83F0 | 04 | read | 113 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-121 | Group：4 Member： 0:no event 1：Power down event
1010 | 33777 | 83F1 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-34
1011 | 33778 | 83F2 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-45
1012 | 33779 | 83F3 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-81
1013 | 33780 | 83F4 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1022
1014 | 33781 | 83F5 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1015 | 33782 | 83F6
1016 | 33783 | 83F7 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1017 | 33784 | 83F8
1018 | 33785 | 83F9 | 04 | read | 114 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-122
1019 | 33786 | 83FA | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-35
1020 | 33787 | 83FB | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-46
1021 | 33788 | 83FC | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-82
1022 | 33789 | 83FD | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1023
1023 | 33790 | 83FE | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1024 | 33791 | 83FF
1025 | 33792 | 8400 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1026 | 33793 | 8401
1027 | 33794 | 8402 | 04 | read | 115 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-123 | Group：5 Member： 0:no event 1：Electricity event 2：Self-checking event 3：Parameter modification event 4：Password change event 5：Event clear event
1028 | 33795 | 8403 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-36
1029 | 33796 | 8404 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-47
1030 | 33797 | 8405 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-83
1031 | 33798 | 8406 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1024
1032 | 33799 | 8407 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1033 | 33800 | 8408
1034 | 33801 | 8409 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1035 | 33802 | 840A
1036 | 33803 | 840B | 04 | read | 116 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-124
1037 | 33804 | 840C | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-37
1038 | 33805 | 840D | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-48
1039 | 33806 | 840E | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-84
1040 | 33807 | 840F | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1025
1041 | 33808 | 8410 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1042 | 33809 | 8411
1043 | 33810 | 8412 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1044 | 33811 | 8413
1045 | 33812 | 8414 | 04 | read | 117 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-125
1046 | 33813 | 8415 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-38
1047 | 33814 | 8416 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-49
1048 | 33815 | 8417 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-85
1049 | 33816 | 8418 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1026
1050 | 33817 | 8419 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1051 | 33818 | 841A
1052 | 33819 | 841B | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1053 | 33820 | 841C
1054 | 33821 | 841D | 04 | read | 118 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-126
1055 | 33822 | 841E | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-39
1056 | 33823 | 841F | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-50
1057 | 33824 | 8420 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-86
1058 | 33825 | 8421 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1027
1059 | 33826 | 8422 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1060 | 33827 | 8423
1061 | 33828 | 8424 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1062 | 33829 | 8425
1063 | 33830 | 8426 | 04 | read | 119 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-127
1064 | 33831 | 8427 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-40
1065 | 33832 | 8428 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-51
1066 | 33833 | 8429 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-87
1067 | 33834 | 842A | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1028
1068 | 33835 | 842B | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1069 | 33836 | 842C
1070 | 33837 | 842D | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1071 | 33838 | 842E
1072 | 33839 | 842F | 04 | read | 120 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-128
1073 | 33840 | 8430 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-41
1074 | 33841 | 8431 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-52
1075 | 33842 | 8432 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-88
1076 | 33843 | 8433 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1029
1077 | 33844 | 8434 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1078 | 33845 | 8435
1079 | 33846 | 8436 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1080 | 33847 | 8437
1081 | 33848 | 8438 | 04 | read | 121 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-129
1082 | 33849 | 8439 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-42
1083 | 33850 | 843A | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-53
1084 | 33851 | 843B | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-89
1085 | 33852 | 843C | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1030
1086 | 33853 | 843D | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1087 | 33854 | 843E
1088 | 33855 | 843F | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1089 | 33856 | 8440
1090 | 33857 | 8441 | 04 | read | 122 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-130
1091 | 33858 | 8442 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-43
1092 | 33859 | 8443 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-54
1093 | 33860 | 8444 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-90
1094 | 33861 | 8445 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1031
1095 | 33862 | 8446 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1096 | 33863 | 8447
1097 | 33864 | 8448 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1098 | 33865 | 8449
1099 | 33866 | 844A | 04 | read | 123 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-131
1100 | 33867 | 844B | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-44
1101 | 33868 | 844C | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-55
1102 | 33869 | 844D | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-91
1103 | 33870 | 844E | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1032
1104 | 33871 | 844F | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1105 | 33872 | 8450
1106 | 33873 | 8451 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1107 | 33874 | 8452
1108 | 33875 | 8453 | 04 | read | 124 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-132
1109 | 33876 | 8454 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-45
1110 | 33877 | 8455 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-56
1111 | 33878 | 8456 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-92
1112 | 33879 | 8457 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1033
1113 | 33880 | 8458 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1114 | 33881 | 8459
1115 | 33882 | 845A | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1116 | 33883 | 845B
1117 | 33884 | 845C | 04 | read | 125 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-133
1118 | 33885 | 845D | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-46
1119 | 33886 | 845E | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-57
1120 | 33887 | 845F | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-93
1121 | 33888 | 8460 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1034
1122 | 33889 | 8461 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1123 | 33890 | 8462
1124 | 33891 | 8463 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1125 | 33892 | 8464
1126 | 33893 | 8465 | 04 | read | 126 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-134
1127 | 33894 | 8466 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-47
1128 | 33895 | 8467 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-58
1129 | 33896 | 8468 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-94
1130 | 33897 | 8469 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1035
1131 | 33898 | 846A | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1132 | 33899 | 846B
1133 | 33900 | 846C | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1134 | 33901 | 846D
1135 | 33902 | 846E | 04 | read | 127 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-135
1136 | 33903 | 846F | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-48
1137 | 33904 | 8470 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-59
1138 | 33905 | 8471 | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-95
1139 | 33906 | 8472 | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1036
1140 | 33907 | 8473 | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1141 | 33908 | 8474
1142 | 33909 | 8475 | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1143 | 33910 | 8476
1144 | 33911 | 8477 | 04 | read | 128 | Event Type（group，member） | unsigned 16 bit | 0 | high bit 0-37，low bit 0-136
1145 | 33912 | 8478 | 04 | read |  | Occur Time（year，month） | unsigned 16 bit | 0 | high bit 0-99，low bit 1-49
1146 | 33913 | 8479 | 04 | read |  | Occur Time（day，hour） | unsigned 16 bit | 0 | high bit 1-31，low bit 0-60
1147 | 33914 | 847A | 04 | read |  | Occur Time（minute，second） | unsigned 16 bit | 0 | high bit 0-59，low bit 0-96
1148 | 33915 | 847B | 04 | read |  | Occur Time（millsecond） | unsigned 16 bit | 0 | 0-1037
1149 | 33916 | 847C | 04 | read |  | Alarm Value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1150 | 33917 | 847D
1151 | 33918 | 847E | 04 | read |  | Alarm limit value | unsigned 32 bit | 0 | 0~0xFFFFFFFF
1152 | 33919 | 847F

## FXXX Zone
Alarm Reset
NO | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Type | Parameters |  | Data Type | Default | Value Range
1 | 61440 | F000 | 06 | write | Alarm Reset | Alarm Reset | U16 | 0 | 0-1
2 | 61441 | F001 | 06 | write | Automatic System Check | Automatic System Check | U16 | 0 | 0-1
3 | 61442 | F002 | 06 | write | Silencer | Silencer | U16 | 0 | 0-1