## DI DO
DI（Function Code 02, read）
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
0 | 0 | Digital Input (read) | DI1 | 0 | 0~1
1 | 1 |  | DI2 | 0 | 0~1
2 | 2 |  | DI3 | 0 | 0~1
3 | 3 |  | DI4 | 0 | 0~1
0: open;1: closed）
DO（function code 01H、05H）
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
2048 | 0800 | DO （read/write） | Relay 1 | 0 | 0~1
2049 | 0801 |  | Relay 2 | 0 | 0~1
0: open;1: closed）
function code 05 ：01 05 08 00 00 00 CRCH CRCL-set relay 1 as off
01 05 08 01 FF 00 CRCH CRCL-set relay 2 as on
DO status（fucntion code 05H write）
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
20480 | 5000 | DO （write） | Relay 1 | FF00= ON
0000= OFF
20481 | 5001 |  | Relay 2 | FF00= ON
0000= OFF

## 0x1000
Basic Parameters Measured Zone（Function Code 04 Read）Secondary
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
4096 | 1000 | Phase Voltage | phase A voltage | magnifying 100 times | 0~65535
4097 | 1001 |  | phase B voltage | magnifying 100 times | 0~65535
4098 | 1002 |  | phase C voltage | magnifying 100 times | 0~65535
4099 | 1003 |  | phase voltage mean value | magnifying 100 times | 0~65535
4100 | 1004 |  | zero sequence voltage | magnifying 100 times | 0~65535
4101 | 1005 | Line Voltage | line voltage(A-B) | magnifying 100 times | 0~65535
4102 | 1006 |  | line voltage(B-C) | magnifying 100 times | 0~65535
4103 | 1007 |  | line voltage(C-A) | magnifying 100 times | 0~65535
4104 | 1008 |  | line voltage mean value | magnifying 100 times | 0~65535
4105 | 1009 | Current | phase/line Current of phase A | magnifying 1,000 times | 0~65535
4106 | 100A |  | phase/line Current of phase B | magnifying 1,000 times | 0~65535
4107 | 100B |  | phase/line Current of phase C | magnifying 1,000 times | 0~65535
4108 | 100C |  | phase/line Current mean value | magnifying 1,000 times | 0~65535
4109 | 100D |  | zero sequence current | magnifying 1,000 times | 0~65535
4110 | 100E | Active Power | active power of phase A | magnifying 1,000 times | -32768~32767
4111 | 100F |  | active power of phase B | magnifying 1,000 times | -32768~32767
4112 | 1010 |  | active power of phase C | magnifying 1,000 times | -32768~32767
4113 | 1011 |  | total three-phase active power | magnifying 1,000 times | -32768~32767
4114 | 1012 | Reactive Power | reactive power of phase A | magnifying 1,000 times | -32768~32767
4115 | 1013 |  | reactive power of phase B | magnifying 1,000 times | -32768~32767
4116 | 1014 |  | reactive power of phase C | magnifying 1,000 times | -32768~32767
4117 | 1015 |  | total three-phase reactive power | magnifying 1,000 times | -32768~32767
4118 | 1016 | Apparent Power | apparent power of phase A | magnifying 1,000 times | -32768~32767
4119 | 1017 |  | apparent power of phase B | magnifying 1,000 times | -32768~32767
4120 | 1018 |  | apparent power of phase C | magnifying 1,000 times | -32768~32767
4121 | 1019 |  | total three-phase apparent power | magnifying 1,000 times | -32768~32767
4122 | 101A | Power Factor | power factor of phase A | magnifying 1,000 times | -1000~1000
4123 | 101B |  | power factor of phase B | magnifying 1,000 times | -1000~1000
4124 | 101C |  | power factor of phase C | magnifying 1,000 times | -1000~1000
4125 | 101D |  | total three-phase power factor | magnifying 1,000 times | -1000~1000
4126 | 101E | Frequency | Frequency | magnifying 100 times | 0~65535
4127 | 101F | Unbalance Factor | Voltage Unbalance Factor | magnifying 100 times | 0~65535
4128 | 1020 |  | Current Unbalance Factor | magnifying 100 times | 0~65535
Basic Parameters Measured Zone（Function Code 04 Read）Primary
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
5376 | 1500 | Phase Voltage | phase A voltage | magnifying 100 times | 0~4294967295
5377 | 1501
5378 | 1502 |  | phase B voltage | magnifying 100 times | 0~4294967295
5379 | 1503
5380 | 1504 |  | phase C voltage | magnifying 100 times | 0~4294967295
5381 | 1505
5382 | 1506 |  | phase voltage mean value | magnifying 100 times | 0~4294967295
5383 | 1507
5384 | 1508 |  | zero sequence voltage | magnifying 100 times | 0~4294967295
5385 | 1509
5386 | 150A | line voltage | line voltage(A-B) | magnifying 100 times | 0~4294967295
5387 | 150B
5388 | 150C |  | line voltage(B-C) | magnifying 100 times | 0~4294967295
5389 | 150D
5390 | 150E |  | line voltage(C-A) | magnifying 100 times | 0~4294967295
5391 | 150F
5392 | 1510 |  | line voltage mean value | magnifying 100 times | 0~4294967295
5393 | 1511
5394 | 1512 | Current | phase A Current | magnifying 1,000 times | 0~4294967295
5395 | 1513
5396 | 1514 |  | phase B Current | magnifying 1,000 times | 0~4294967295
5397 | 1515
5398 | 1516 |  | phase C Current | magnifying 1,000 times | 0~4294967295
5399 | 1517
5400 | 1518 |  | phase Current mean value | magnifying 1,000 times | 0~4294967295
5401 | 1519
5402 | 151A |  | zero sequence voltage | magnifying 1,000 times | 0~4294967295
5403 | 151B
5404 | 151C | Active Power | active power of phase A | magnifying 1,000 times | -2147483647~2147483647
5405 | 151D
5406 | 151E |  | active power of phase B | magnifying 1,000 times | -2147483647~2147483647
5407 | 151F
5408 | 1520 |  | active power of phase C | magnifying 1,000 times | -2147483647~2147483647
5409 | 1521
5410 | 1522 |  | total three-phase active power | magnifying 1,000 times | -2147483647~2147483647
5411 | 1523
5412 | 1524 | Reactive Power | reactive power of phase A | magnifying 1,000 times | -2147483647~2147483647
5413 | 1525
5414 | 1526 |  | reactive power of phase B | magnifying 1,000 times | -2147483647~2147483647
5415 | 1527
5416 | 1528 |  | reactive power of phase C | magnifying 1,000 times | -2147483647~2147483647
5417 | 1529
5418 | 152A |  | total three-phase reactive power | magnifying 1,000 times | -2147483647~2147483647
5419 | 152B
5420 | 152C | apparent power | apparent power of phase A | magnifying 1,000 times | 0~4294967295
5421 | 152D
5422 | 152E |  | apparent power of phase B | magnifying 1,000 times | 0~4294967295
5423 | 152F
5424 | 1530 |  | apparent power of phase C | magnifying 1,000 times | 0~4294967295
5425 | 1531
5426 | 1532 |  | total three-phase apparent power | magnifying 1,000 times | 0~4294967295
5427 | 1533
5428 | 1534 | power factor | power factor of phase A | magnifying 1,000 times | -1000~1000
5429 | 1535 |  | power factor of phase B | magnifying 1,000 times | -1000~1000
5430 | 1536 |  | power factor of phase C | magnifying 1,000 times | -1000~1000
5431 | 1537 |  | total three-phase power factor | magnifying 1,000 times | -1000~1000
5432 | 1538 | Frequency | Frequency | magnifying 100 times | 0~65535
Remark: 1.Primary Voltage Value = Secondary Voltage Value * PT 2.Primary Current Value = Secondary Current Value * CT 3.Primary Power Value = Secondary Power Value * PT * CT
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
4352 | 1100 | Total Harmonic Distortion Rate (THD) | line/phase voltage THD of phase A | magnifying 1,000 times | 0~10000
4353 | 1101 |  | line/phase voltage THD of phase B | magnifying 1,000 times | 0~10000
4354 | 1102 |  | line/phase voltage THD of phase C | magnifying 1,000 times | 0~10000
4355 | 1103 |  | line/phase voltage mean value THD | magnifying 1,000 times | 0~10000
4356 | 1104 |  | current THD of phase A | magnifying 1,000 times | 0~10000
4357 | 1105 |  | current THD of phase B | magnifying 1,000 times | 0~10000
4358 | 1106 |  | current THD of phase C | magnifying 1,000 times | 0~10000
4359 | 1107 |  | current mean value THD | magnifying 1,000 times | 0~10000
4360 | 1108 | (Odd) Phase A Voltage Harmonic Content | 3rd line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4361 | 1109 |  | 5th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4362 | 110A |  | 7th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4363 | 110B |  | 9th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4364 | 110C |  | 11th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4365 | 110D |  | 13th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4366 | 110E |  | 15th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4367 | 110F |  | 17th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4368 | 1110 |  | 19th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4369 | 1111 |  | 21st line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4370 | 1112 |  | 23rd line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4371 | 1113 |  | 25th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4372 | 1114 |  | 27th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4373 | 1115 |  | 29th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4374 | 1116 |  | 31st line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4375 | 1117 | (Even) Phase A Voltage Harmonic Content | 2nd line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4376 | 1118 |  | 4th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4377 | 1119 |  | 6th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4378 | 111A |  | 8th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4379 | 111B |  | 10th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4380 | 111C |  | 12th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4381 | 111D |  | 14th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4382 | 111E |  | 16th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4383 | 111F |  | 18th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4384 | 1120 |  | 20th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4385 | 1121 |  | 22nd line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4386 | 1122 |  | 24th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4387 | 1123 |  | 26th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4388 | 1124 |  | 28th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4389 | 1125 |  | 30th line/phase voltage harmonic content of Phase A | magnifying 1,000 times | 0~10000
4390 | 1126 | Phase A Voltage Harmonic Analysis | odd line/phase voltage harmonic distortion rate of Phase A | magnifying 1,000 times | 0~10000
4391 | 1127 |  | even line/phase voltage harmonic distortion rate of Phase A | magnifying 1,000 times | 0~10000
4392 | 1128 |  | line/phase voltage crest factor of Phase A | magnifying 1,000 times | 0~10000
4393 | 1129 |  | reserved | magnifying 1,000 times | 0~10000
4394 | 112A | Phase B Voltage(Odd) Harmonic Content | 3rd line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4395 | 112B |  | 5th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4396 | 112C |  | 7th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4397 | 112D |  | 9th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4398 | 112E |  | 11th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4399 | 112F |  | 13th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4400 | 1130 |  | 15th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4401 | 1131 |  | 17th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4402 | 1132 |  | 19th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4403 | 1133 |  | 21st line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4404 | 1134 |  | 23rd line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4405 | 1135 |  | 25th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4406 | 1136 |  | 27th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4407 | 1137 |  | 29th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4408 | 1138 |  | 31st line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4409 | 1139 | (Even) Phase B Voltage Harmonic Content | 2nd line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4410 | 113A |  | 4th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4411 | 113B |  | 6th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4412 | 113C |  | 8th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4413 | 113D |  | 10th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4414 | 113E |  | 12th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4415 | 113F |  | 14th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4416 | 1140 |  | 16th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4417 | 1141 |  | 18th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4418 | 1142 |  | 20th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4419 | 1143 |  | 22nd line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4420 | 1144 |  | 24th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4421 | 1145 |  | 26th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4422 | 1146 |  | 28th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4423 | 1147 |  | 30th line/phase voltage harmonic content of Phase B | magnifying 1,000 times | 0~10000
4424 | 1148 | Phase B Voltage Harmonic Analysis | odd line/phase voltage harmonic distortion rate of Phase B | magnifying 1,000 times | 0~10000
4425 | 1149 |  | even line/phase voltage harmonic distortion rate of Phase B | magnifying 1,000 times | 0~10000
4426 | 114A |  | line/phase voltage crest factor of Phase A | magnifying 1,000 times | 0~10000
4427 | 114B |  | reserved | magnifying 1,000 times | 0~10000
4428 | 114C | (Odd) Phase C Voltage Harmonic Content | 3rd line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4429 | 114D |  | 5th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4430 | 114E |  | 7th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4431 | 114F |  | 9th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4432 | 1150 |  | 11th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4433 | 1151 |  | 13th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4434 | 1152 |  | 15th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4435 | 1153 |  | 17th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4436 | 1154 |  | 19th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4437 | 1155 |  | 21st line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4438 | 1156 |  | 23rd line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4439 | 1157 |  | 25th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4440 | 1158 |  | 27th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4441 | 1159 |  | 29th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4442 | 115A |  | 31st line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4443 | 115B | (Even) Phase C Voltage Harmonic Content | 2nd line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4444 | 115C |  | 4th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4445 | 115D |  | 6th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4446 | 115E |  | 8th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4447 | 115F |  | 10th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4448 | 1160 |  | 12th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4449 | 1161 |  | 14th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4450 | 1162 |  | 16th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4451 | 1163 |  | 18th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4452 | 1164 |  | 20th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4453 | 1165 |  | 22nd line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4454 | 1166 |  | 24th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4455 | 1167 |  | 26th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4456 | 1168 |  | 28th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4457 | 1169 |  | 30th line/phase voltage harmonic content of Phase C | magnifying 1,000 times | 0~10000
4458 | 116A | Phase C Voltage Harmonic Analysis | odd line/phase voltage harmonic distortion rate of Phase C | magnifying 1,000 times | 0~10000
4459 | 116B |  | even line/phase voltage harmonic distortion rate of Phase C | magnifying 1,000 times | 0~10000
4460 | 116C |  | line/phase voltage crest factor of Phase C | magnifying 1,000 times | 0~10000
4461 | 116D |  | reserved | magnifying 1,000 times | 0~10000
4462 | 116E | (Odd) Phase A Current Harmonic Content | 3rd current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4463 | 116F |  | 5th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4464 | 1170 |  | 7th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4465 | 1171 |  | 9th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4466 | 1172 |  | 11th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4467 | 1173 |  | 13th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4468 | 1174 |  | 15th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4469 | 1175 |  | 17th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4470 | 1176 |  | 19th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4471 | 1177 |  | 21st current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4472 | 1178 |  | 23rd current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4473 | 1179 |  | 25th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4474 | 117A |  | 27th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4475 | 117B |  | 29th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4476 | 117C |  | 31st current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4477 | 117D | (Even) Phase A Current Harmonic Content | 2nd current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4478 | 117E |  | 4th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4479 | 117F |  | 6th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4480 | 1180 |  | 8th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4481 | 1181 |  | 10th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4482 | 1182 |  | 12th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4483 | 1183 |  | 14th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4484 | 1184 |  | 16th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4485 | 1185 |  | 18th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4486 | 1186 |  | 20th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4487 | 1187 |  | 22nd current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4488 | 1188 |  | 24th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4489 | 1189 |  | 26th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4490 | 118A |  | 28th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4491 | 118B |  | 30th current harmonic content of Phase A | magnifying 1,000 times | 0~10000
4492 | 118C | Phase A Current Harmonic Analysis | odd current harmonic distortion rate of Phase A | magnifying 1,000 times | 0~10000
4493 | 118D |  | even current harmonic distortion rate of Phase A | magnifying 1,000 times | 0~10000
4494 | 118E |  | reserved | magnifying 1,000 times | 0~10000
4495 | 118F | (Odd) Phase B Current Harmonic Content | 3rd current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4496 | 1190 |  | 5th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4497 | 1191 |  | 7th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4498 | 1192 |  | 9th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4499 | 1193 |  | 11th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4500 | 1194 |  | 13th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4501 | 1195 |  | 15th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4502 | 1196 |  | 17th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4503 | 1197 |  | 19th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4504 | 1198 |  | 21st current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4505 | 1199 |  | 23rd current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4506 | 119A |  | 25th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4507 | 119B |  | 27th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4508 | 119C |  | 29th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4509 | 119D |  | 31st current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4510 | 119E | (Even) Phase B Current Harmonic Content | 2nd current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4511 | 119F |  | 4th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4512 | 11A0 |  | 6th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4513 | 11A1 |  | 8th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4514 | 11A2 |  | 10th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4515 | 11A3 |  | 12th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4516 | 11A4 |  | 14th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4517 | 11A5 |  | 16th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4518 | 11A6 |  | 18th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4519 | 11A7 |  | 20th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4520 | 11A8 |  | 22nd current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4521 | 11A9 |  | 24th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4522 | 11AA |  | 26th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4523 | 11AB |  | 28th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4524 | 11AC |  | 30th current harmonic content of Phase B | magnifying 1,000 times | 0~10000
4525 | 11AD | Phase B Current Harmonic Analysis | odd current harmonic distortion rate of Phase B | magnifying 1,000 times | 0~10000
4526 | 11AE |  | even current harmonic distortion rate of Phase B | magnifying 1,000 times | 0~10000
4527 | 11AF |  | reserved | magnifying 1,000 times | 0~10000
4528 | 11B0 | (Odd) Phase C Current Harmonic Content | 3rd current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4529 | 11B1 |  | 5th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4530 | 11B2 |  | 7th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4531 | 11B3 |  | 9th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4532 | 11B4 |  | 11th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4533 | 11B5 |  | 13th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4534 | 11B6 |  | 15th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4535 | 11B7 |  | 17th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4536 | 11B8 |  | 19th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4537 | 11B9 |  | 21st current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4538 | 11BA |  | 23rd current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4539 | 11BB |  | 25th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4540 | 11BC |  | 27th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4541 | 11BD |  | 29th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4542 | 11BE |  | 31st current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4543 | 11BF | (Even) Phase C Current Harmonic Content | 2nd current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4544 | 11C0 |  | 4th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4545 | 11C1 |  | 6th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4546 | 11C2 |  | 8th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4547 | 11C3 |  | 10th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4548 | 11C4 |  | 12th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4549 | 11C5 |  | 14th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4550 | 11C6 |  | 16th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4551 | 11C7 |  | 18th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4552 | 11C8 |  | 20th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4553 | 11C9 |  | 22nd current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4554 | 11CA |  | 24th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4555 | 11CB |  | 26th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4556 | 11CC |  | 28th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4557 | 11CD |  | 30th current harmonic content of Phase C | magnifying 1,000 times | 0~10000
4558 | 11CE | Phase C Current Harmonic Analysis | odd current harmonic distortion rate of Phase C | magnifying 1,000 times | 0~10000
4559 | 11CF |  | even current harmonic distortion rate of Phase C | magnifying 1,000 times | 0~10000
4560 | 11D0 |  | reserved | magnifying 1,000 times
Remark： 1. The registers, named as "Reserved", in the harmonic parameter zone, have no function in this meter. And the data read from these registers can not be used for any reference, and theses registers are only reserved for future extended functions. 2. All the data of registers from 0x1100 to 0x11D0 are magnified 1000 times.

## 0x2000
Address (Decimal) | Address (Hexadecimal) | Parameter | Default | Value Range
8192 | 2000 | password protection (protection of basic parameters) | 0 | 0000~9999
8193 | 2001 | meter communication address | 1 | 1~253
8194 | 2002 | Baud Rate | 3 | 0:1200,1:2400,2:4800,3:9600,
8195 | 2003 | serial port parameter | 0 | 0:(8n1),1:(8o1),2:(8e1)
8196 | 2004 | voltage wiring mode | 0 | 0：3LN(3P4W)
1：2LL(3P3W)
8197 | 2005 | current wiring mode | 1 | 0：3CT，1：2CT
8198 | 2006 | PT | 1 | 1~1100
8198 | 2007 | CT | 1 | 1~2000
8200 | 2008 | backlight time | 30 | 0~999（0：Always ON）
8201 | 2009 | DO1 Setting | 0 | 0：Electrical Level，1：pulse；
8202 | 200A | DO2 Setting | 0 | 0：Electrical Level，1：pulse；
8203 | 200B | Reserved | 0x0100 | Reserved
8204 | 200C | energy ratio switch | 0 | 0：closed(secondary energy)， 1：open(primary energy)
8205 | 200D | Number of decimal places for energy | 1 | 1~3
Remark： The product of CT and PT should be less than 300,000.

## 0x3000
Real-time Clock Zone（（Function Code 0x10 Write; Function Code 03 Read）
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
12800 | 3200 | Time | Year | 2020 | 2000~2099
12801 | 3201 |  | Month | 1 | 1~12
12802 | 3202 |  | Date | 1 | 1~31
12803 | 3203 |  | Hour | 0 | 0~23
12804 | 3204 |  | Minite | 0 | 0~59
12805 | 3205 |  | Second | 0 | 0~59

## 0x4000
0x4000 parameter Zone（Function Code 04，only read）
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
16进制
16384 | 4000 | Total Real-time Energy (Secondary side) | Total Active Energy | 0 | 0~9999999.9
16385 | 4001
16386 | 4002 |  | Import Active Energy | 0 | 0~9999999.9
16387 | 4003
16388 | 4004 |  | Export Active Energy | 0 | 0~9999999.9
16389 | 4005
16390 | 4006 |  | Total Reactive Energy | 0 | 0`9999999.9
16391 | 4007
16392 | 4008 |  | Import Reactive Energy | 0 | 0~9999999.9
16393 | 4009
16394 | 400A |  | Export Reactive Energy | 0 | 0~9999999.9
16395 | 400B
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
17664 | 4500 | Total Real-time Energy (Primary side) | Total Active Energy | 0 | 0~99999999999.9
17665 | 4501
17666 | 4502
17667 | 4503 |  | Import Active Energy | 0 | 0~99999999999.9
17668 | 4504 |  |  | 0 | 0~99999999999.9
17669 | 4505
17670 | 4506 |  | Export Active Energy | 0 | 0~99999999999.9
17671 | 4507
17672 | 4508 |  | Export Active Energy
17673 | 4509 |  | Total Reactive Energy | 0 | 0~99999999999.9
17674 | 450A |  | Export Active Energy
17675 | 450B |  | Export Active Energy
17676 | 450C |  | Import Reactive Energy | 0 | 0~99999999999.9
17677 | 450D |  | Total Reactive Energy
17678 | 450E |  | Total Reactive Energy
17679 | 450F |  | Export Reactive Energy | 0 | 0~99999999999.9
17680 | 4510 |  | Import Reactive Energy
17681 | 4511 |  | Import Reactive Energy
Address (Decimal) | Address (Hexadecimal) | Category | Parameter | Default | Value Range
16640 | 4100 | Present-month Energy (Total） | Total Active Energy | 0 | 0~9999999.9
16641 | 4101
16642 | 4102 |  | Import Active Energy | 0 | 0~9999999.9
16643 | 4103
16644 | 4104 |  | Export Active Energy | 0 | 0~9999999.9
16645 | 4105
16646 | 4106 |  | Total Reactive Energy | 0 | 0~9999999.9
16647 | 4107
16648 | 4108 |  | Import Reactive Energy | 0 | 0~9999999.9
16649 | 4109
16650 | 410A |  | Export Reactive Energy | 0 | 0~9999999.9
16651 | 410B
16652 | 410C | Present-month Energy (Sharp） | Total Active Energy | 0 | 0~9999999.9
16653 | 410D
16654 | 410E |  | Import Active Energy | 0 | 0~9999999.9
16655 | 410F
16656 | 4110 |  | Export Active Energy | 0 | 0~9999999.9
16657 | 4111
16658 | 4112 |  | Total Reactive Energy | 0 | 0~9999999.9
16659 | 4113
16660 | 4114 |  | Import Reactive Energy | 0 | 0~9999999.9
16661 | 4115
16662 | 4116 |  | Export Reactive Energy | 0 | 0~9999999.9
16663 | 4117
16664 | 4118 | Present-month Energy (Peak） | Total Active Energy | 0 | 0~9999999.9
16665 | 4119
16666 | 411A |  | Import Active Energy | 0 | 0~9999999.9
16667 | 411B
16668 | 411C |  | Export Active Energy | 0 | 0~9999999.9
16669 | 411D
16670 | 411E |  | Total Reactive Energy | 0 | 0~9999999.9
16671 | 411F
16672 | 4120 |  | Import Reactive Energy | 0 | 0~9999999.9
16673 | 4121
16674 | 4122 |  | Export Reactive Energy | 0 | 0~9999999.9
16675 | 4123
16676 | 4124 | Present-month Energy (Off-peak） | Total Active Energy | 0 | 0~9999999.9
16677 | 4125
16678 | 4126 |  | Import Active Energy | 0 | 0~9999999.9
16679 | 4127
16680 | 4128 |  | Export Active Energy | 0 | 0~9999999.9
16681 | 4129
16682 | 412A |  | Total Reactive Energy | 0 | 0~9999999.9
16683 | 412B
16684 | 412C |  | Import Reactive Energy | 0 | 0~9999999.9
16685 | 412D
16686 | 412E |  | Export Reactive Energy | 0 | 0~9999999.9
16687 | 412F
16688 | 4130 | Present-month Energy (shoulder) | Total Active Energy | 0 | 0~9999999.9
16689 | 4131
16690 | 4132 |  | Import Active Energy | 0 | 0~9999999.9
16691 | 4133
16692 | 4134 |  | Export Active Energy | 0 | 0~9999999.9
16693 | 4135
16694 | 4136 |  | Total Reactive Energy | 0 | 0~9999999.9
16695 | 4137
16696 | 4138 |  | Import Reactive Energy | 0 | 0~9999999.9
16697 | 4139
16698 | 413A |  | Export Reactive Energy | 0 | 0~9999999.9
16699 | 413B
16700 | 413C | Last 1st month Energy (Total） | Total Active Energy | 0 | 0~9999999.9
16701 | 413D
16702 | 413E |  | Import Active Energy | 0 | 0~9999999.9
16703 | 413F
16704 | 4140 |  | Export Active Energy | 0 | 0~9999999.9
16705 | 4141
16706 | 4142 |  | Total Reactive Energy | 0 | 0~9999999.9
16707 | 4143
16708 | 4144 |  | Import Reactive Energy | 0 | 0~9999999.9
16709 | 4145
16710 | 4146 |  | Export Reactive Energy | 0 | 0~9999999.9
16711 | 4147
16712 | 4148 | Last 1st month Energy (Sharp） | Total Active Energy | 0 | 0~9999999.9
16713 | 4149
16714 | 414A |  | Import Active Energy | 0 | 0~9999999.9
16715 | 414B
16716 | 414C |  | Export Active Energy | 0 | 0~9999999.9
16717 | 414D
16718 | 414E |  | Total Reactive Energy | 0 | 0~9999999.9
16719 | 414F
16720 | 4150 |  | Import Reactive Energy | 0 | 0~9999999.9
16721 | 4151
16722 | 4152 |  | Export Reactive Energy | 0 | 0~9999999.9
16723 | 4153
16724 | 4154 | Last 1st month Energy (Peak） | Total Active Energy | 0 | 0~9999999.9
16725 | 4155
16726 | 4156 |  | Import Active Energy | 0 | 0~9999999.9
16727 | 4157
16728 | 4158 |  | Export Active Energy | 0 | 0~9999999.9
16729 | 4159
16730 | 415A |  | Total Reactive Energy | 0 | 0~9999999.9
16731 | 415B
16732 | 415C |  | Import Reactive Energy | 0 | 0~9999999.9
16733 | 415D
16734 | 415E |  | Export Reactive Energy | 0 | 0~9999999.9
16735 | 415F
16736 | 4160 | Last 1st month Energy (Off-peak） | Total Active Energy | 0 | 0~9999999.9
16737 | 4161
16738 | 4162 |  | Import Active Energy | 0 | 0~9999999.9
16739 | 4163
16740 | 4164 |  | Export Active Energy | 0 | 0~9999999.9
16741 | 4165
16742 | 4166 |  | Total Reactive Energy | 0 | 0~9999999.9
16743 | 4167
16744 | 4168 |  | Import Reactive Energy | 0 | 0~9999999.9
16745 | 4169
16746 | 416A |  | Export Reactive Energy | 0 | 0~9999999.9
16747 | 416B
16748 | 416C | Last 1st month Energy (shoulder) | Total Active Energy | 0 | 0~9999999.9
16749 | 416D
16750 | 416E |  | Import Active Energy | 0 | 0~9999999.9
16751 | 416F
16752 | 4170 |  | Export Active Energy | 0 | 0~9999999.9
16753 | 4171
16754 | 4172 |  | Total Reactive Energy | 0 | 0~9999999.9
16755 | 4173
16756 | 4174 |  | Import Reactive Energy | 0 | 0~9999999.9
16757 | 4175
16758 | 4176 |  | Export Reactive Energy | 0 | 0~9999999.9
16759 | 4177
16760 | 4178 | Last 2nd month Energy (Total） | Total Active Energy | 0 | 0~9999999.9
16761 | 4179
16762 | 417A |  | Import Active Energy | 0 | 0~9999999.9
16763 | 417B
16764 | 417C |  | Export Active Energy | 0 | 0~9999999.9
16765 | 417D
16766 | 417E |  | Total Reactive Energy | 0 | 0~9999999.9
16767 | 417F
16768 | 4180 |  | Import Reactive Energy | 0 | 0~9999999.9
16769 | 4181
16770 | 4182 |  | Export Reactive Energy | 0 | 0~9999999.9
16771 | 4183
16772 | 4184 | Last 2nd month Energy (Sharp） | Total Active Energy | 0 | 0~9999999.9
16773 | 4185
16774 | 4186 |  | Import Active Energy | 0 | 0~9999999.9
16775 | 4187
16776 | 4188 |  | Export Active Energy | 0 | 0~9999999.9
16777 | 4189
16778 | 418A |  | Total Reactive Energy | 0 | 0~9999999.9
16779 | 418B
16780 | 418C |  | Import Reactive Energy | 0 | 0~9999999.9
16781 | 418D
16782 | 418E |  | Export Reactive Energy | 0 | 0~9999999.9
16783 | 418F
16784 | 4190 | Last 2nd month Energy (Peak） | Total Active Energy | 0 | 0~9999999.9
16785 | 4191
16786 | 4192 |  | Import Active Energy | 0 | 0~9999999.9
16787 | 4193
16788 | 4194 |  | Export Active Energy | 0 | 0~9999999.9
16789 | 4195
16790 | 4196 |  | Total Reactive Energy | 0 | 0~9999999.9
16791 | 4197
16792 | 4198 |  | Import Reactive Energy | 0 | 0~9999999.9
16793 | 4199
16794 | 419A |  | Export Reactive Energy | 0 | 0~9999999.9
16795 | 419B
16796 | 419C | Last 2nd month Energy (Off-peak） | Total Active Energy | 0 | 0~9999999.9
16797 | 419D
16798 | 419E |  | Import Active Energy | 0 | 0~9999999.9
16799 | 419F
16800 | 41A0 |  | Export Active Energy | 0 | 0~9999999.9
16801 | 41A1
16802 | 41A2 |  | Total Reactive Energy | 0 | 0~9999999.9
16803 | 41A3
16804 | 41A4 |  | Import Reactive Energy | 0 | 0~9999999.9
16805 | 41A5
16806 | 41A6 |  | Export Reactive Energy | 0 | 0~9999999.9
16807 | 41A7
16808 | 41A8 | Last 2nd month Energy (shoulder) | Total Active Energy | 0 | 0~9999999.9
16809 | 41A9
16810 | 41AA |  | Import Active Energy | 0 | 0~9999999.9
16811 | 41AB
16812 | 41AC |  | Export Active Energy | 0 | 0~9999999.9
16813 | 41AD
16814 | 41AE |  | Total Reactive Energy | 0 | 0~9999999.9
16815 | 41AF
16816 | 41B0 |  | Import Reactive Energy | 0 | 0~9999999.9
16817 | 41B1
16818 | 41B2 |  | Export Reactive Energy | 0 | 0~9999999.9
16819 | 41B3
16820 | 41B4 | Last 3rd month Energy (Total） | Total Active Energy | 0 | 0~9999999.9
16821 | 41B5
16822 | 41B6 |  | Import Active Energy | 0 | 0~9999999.9
16823 | 41B7
16824 | 41B8 |  | Export Active Energy | 0 | 0~9999999.9
16825 | 41B9
16826 | 41BA |  | Total Reactive Energy | 0 | 0~9999999.9
16827 | 41BB
16828 | 41BC |  | Import Reactive Energy | 0 | 0~9999999.9
16829 | 41BD
16830 | 41BE |  | Export Reactive Energy | 0 | 0~9999999.9
16831 | 41BF
16832 | 41C0 | Last 3rd month Energy (Sharp） | Total Active Energy | 0 | 0~9999999.9
16833 | 41C1
16834 | 41C2 |  | Import Active Energy | 0 | 0~9999999.9
16835 | 41C3
16836 | 41C4 |  | Export Active Energy | 0 | 0~9999999.9
16837 | 41C5
16838 | 41C6 |  | Total Reactive Energy | 0 | 0~9999999.9
16839 | 41C7
16840 | 41C8 |  | Import Reactive Energy | 0 | 0~9999999.9
16841 | 41C9
16842 | 41CA |  | Export Reactive Energy | 0 | 0~9999999.9
16843 | 41CB
16844 | 41CC | Last 3rd month Energy (Peak） | Total Active Energy | 0 | 0~9999999.9
16845 | 41CD
16846 | 41CE |  | Import Active Energy | 0 | 0~9999999.9
16847 | 41CF
16848 | 41D0 |  | Export Active Energy | 0 | 0~9999999.9
16849 | 41D1
16850 | 41D2 |  | Total Reactive Energy | 0 | 0~9999999.9
16851 | 41D3
16852 | 41D4 |  | Import Reactive Energy | 0 | 0~9999999.9
16853 | 41D5
16854 | 41D6 |  | Export Reactive Energy | 0 | 0~9999999.9
16855 | 41D7
16856 | 41D8 | Last 3rd month Energy (Off-peak） | Total Active Energy | 0 | 0~9999999.9
16857 | 41D9
16858 | 41DA |  | Import Active Energy | 0 | 0~9999999.9
16859 | 41DB
16860 | 41DC |  | Export Active Energy | 0 | 0~9999999.9
16861 | 41DD
16862 | 41DE |  | Total Reactive Energy | 0 | 0~9999999.9
16863 | 41DF
16864 | 41 |  | Import Reactive Energy | 0 | 0~9999999.9
16865 | 410
16866 | 4100 |  | Export Reactive Energy | 0 | 0~9999999.9
16867 | 41000
16868 | 410000 | Last 3rd month Energy (shoulder) | Total Active Energy | 0 | 0~9999999.9
16869 | 4100000
16870 | 41000000 |  | Import Active Energy | 0 | 0~9999999.9
16871 | 410000000
16872 | 4100000000 |  | Export Active Energy | 0 | 0~9999999.9
16873 | 41000000000
16874 | 41EA |  | Total Reactive Energy | 0 | 0~9999999.9
16875 | 41EB
16876 | 41EC |  | Import Reactive Energy | 0 | 0~9999999.9
16877 | 41ED
16878 | 41EE |  | Export Reactive Energy | 0 | 0~9999999.9
16879 | 41EF
16880 | 41F0 | Last 4th month Energy (Total） | Total Active Energy | 0 | 0~9999999.9
16881 | 41F1
16882 | 41F2 |  | Import Active Energy | 0 | 0~9999999.9
16883 | 41F3
16884 | 41F4 |  | Export Active Energy | 0 | 0~9999999.9
16885 | 41F5
16886 | 41F6 |  | Total Reactive Energy | 0 | 0~9999999.9
16887 | 41F7
16888 | 41F8 |  | Import Reactive Energy | 0 | 0~9999999.9
16889 | 41F9
16890 | 41FA |  | Export Reactive Energy | 0 | 0~9999999.9
16891 | 41FB
16892 | 41FC | Last 4th month Energy (Sharp） | Total Active Energy | 0 | 0~9999999.9
16893 | 41FD
16894 | 41FE |  | Import Active Energy | 0 | 0~9999999.9
16895 | 41FF
16896 | 4200 |  | Export Active Energy | 0 | 0~9999999.9
16897 | 4201
16898 | 4202 |  | Total Reactive Energy | 0 | 0~9999999.9
16899 | 4203
16900 | 4204 |  | Import Reactive Energy | 0 | 0~9999999.9
16901 | 4205
16902 | 4206 |  | Export Reactive Energy | 0 | 0~9999999.9
16903 | 4207
16904 | 4208 | Last 4th month Energy (Peak） | Total Active Energy | 0 | 0~9999999.9
16905 | 4209
16906 | 420A |  | Import Active Energy | 0 | 0~9999999.9
16907 | 420B
16908 | 420C |  | Export Active Energy | 0 | 0~9999999.9
16909 | 420D
16910 | 420E |  | Total Reactive Energy | 0 | 0~9999999.9
16911 | 420F
16912 | 4210 |  | Import Reactive Energy | 0 | 0~9999999.9
16913 | 4211
16914 | 4212 |  | Export Reactive Energy | 0 | 0~9999999.9
16915 | 4213
16916 | 4214 | Last 4th month Energy (Off-peak） | Total Active Energy | 0 | 0~9999999.9
16917 | 4215
16918 | 4216 |  | Import Active Energy | 0 | 0~9999999.9
16919 | 4217
16920 | 4218 |  | Export Active Energy | 0 | 0~9999999.9
16921 | 4219
16922 | 421A |  | Total Reactive Energy | 0 | 0~9999999.9
16923 | 421B
16924 | 421C |  | Import Reactive Energy | 0 | 0~9999999.9
16925 | 421D
16926 | 421E |  | Export Reactive Energy | 0 | 0~9999999.9
16927 | 421F
16928 | 4220 | Last 4th month Energy (shoulder) | Total Active Energy | 0 | 0~9999999.9
16929 | 4221
16930 | 4222 |  | Import Active Energy | 0 | 0~9999999.9
16931 | 4223
16932 | 4224 |  | Export Active Energy | 0 | 0~9999999.9
16933 | 4225
16934 | 4226 |  | Total Reactive Energy | 0 | 0~9999999.9
16935 | 4227
16936 | 4228 |  | Import Reactive Energy | 0 | 0~9999999.9
16937 | 4229
16938 | 422A |  | Export Reactive Energy | 0 | 0~9999999.9
16939 | 422B
16940 | 422C | Last 5th month Energy (Total） | Total Active Energy | 0 | 0~9999999.9
16941 | 422D
16942 | 422E |  | Import Active Energy | 0 | 0~9999999.9
16943 | 422F
16944 | 4230 |  | Export Active Energy | 0 | 0~9999999.9
16945 | 4231
16946 | 4232 |  | Total Reactive Energy | 0 | 0~9999999.9
16947 | 4233
16948 | 4234 |  | Import Reactive Energy | 0 | 0~9999999.9
16949 | 4235
16950 | 4236 |  | Export Reactive Energy | 0 | 0~9999999.9
16951 | 4237
16952 | 4238 | Last 5th month Energy (Sharp） | Total Active Energy | 0 | 0~9999999.9
16953 | 4239
16954 | 423A |  | Import Active Energy | 0 | 0~9999999.9
16955 | 423B
16956 | 423C |  | Export Active Energy | 0 | 0~9999999.9
16957 | 423D
16958 | 423E |  | Total Reactive Energy | 0 | 0~9999999.9
16959 | 423F
16960 | 4240 |  | Import Reactive Energy | 0 | 0~9999999.9
16961 | 4241
16962 | 4242 |  | Export Reactive Energy | 0 | 0~9999999.9
16963 | 4243
16964 | 4244 | Last 5th month Energy (Peak） | Total Active Energy | 0 | 0~9999999.9
16965 | 4245
16966 | 4246 |  | Import Active Energy | 0 | 0~9999999.9
16967 | 4247
16968 | 4248 |  | Export Active Energy | 0 | 0~9999999.9
16969 | 4249
16970 | 424A |  | Total Reactive Energy | 0 | 0~9999999.9
16971 | 424B
16972 | 424C |  | Import Reactive Energy | 0 | 0~9999999.9
16973 | 424D
16974 | 424E |  | Export Reactive Energy | 0 | 0~9999999.9
16975 | 424F
16976 | 4250 | Last 5th month Energy (Off-peak） | Total Active Energy | 0 | 0~9999999.9
16977 | 4251
16978 | 4252 |  | Import Active Energy | 0 | 0~9999999.9
16979 | 4253
16980 | 4254 |  | Export Active Energy | 0 | 0~9999999.9
16981 | 4255
16982 | 4256 |  | Total Reactive Energy | 0 | 0~9999999.9
16983 | 4257
16984 | 4258 |  | Import Reactive Energy | 0 | 0~9999999.9
16985 | 4259
16986 | 425A |  | Export Reactive Energy | 0 | 0~9999999.9
16987 | 425B
16988 | 425C | Last 5th month Energy (shoulder) | Total Active Energy | 0 | 0~9999999.9
16989 | 425D
16990 | 425E |  | Import Active Energy | 0 | 0~9999999.9
16991 | 425F
16992 | 4260 |  | Export Active Energy | 0 | 0~9999999.9
16993 | 4261
16994 | 4262 |  | Total Reactive Energy | 0 | 0~9999999.9
16995 | 4263
16996 | 4264 |  | Import Reactive Energy | 0 | 0~9999999.9
16997 | 4265
16998 | 4266 |  | Export Reactive Energy | 0 | 0~9999999.9
16999 | 4267
17000 | 4268 | Last 6th month Energy (Total） | Total Active Energy | 0 | 0~9999999.9
17001 | 4269
17002 | 426A |  | Import Active Energy | 0 | 0~9999999.9
17003 | 426B
17004 | 426C |  | Export Active Energy | 0 | 0~9999999.9
17005 | 426D
17006 | 426E |  | Total Reactive Energy | 0 | 0~9999999.9
17007 | 426F
17008 | 4270 |  | Import Reactive Energy | 0 | 0~9999999.9
17009 | 4271
17010 | 4272 |  | Export Reactive Energy | 0 | 0~9999999.9
17011 | 4273
17012 | 4274 | Last 6th month Energy (Sharp） | Total Active Energy | 0 | 0~9999999.9
17013 | 4275
17014 | 4276 |  | Import Active Energy | 0 | 0~9999999.9
17015 | 4277
17016 | 4278 |  | Export Active Energy | 0 | 0~9999999.9
17017 | 4279
17018 | 427A |  | Total Reactive Energy | 0 | 0~9999999.9
17019 | 427B
17020 | 427C |  | Import Reactive Energy | 0 | 0~9999999.9
17021 | 427D
17022 | 427E |  | Export Reactive Energy | 0 | 0~9999999.9
17023 | 427F
17024 | 4280 | Last 6th month Energy (Peak） | Total Active Energy | 0 | 0~9999999.9
17025 | 4281
17026 | 4282 |  | Import Active Energy | 0 | 0~9999999.9
17027 | 4283
17028 | 4284 |  | Export Active Energy | 0 | 0~9999999.9
17029 | 4285
17030 | 4286 |  | Total Reactive Energy | 0 | 0~9999999.9
17031 | 4287
17032 | 4288 |  | Import Reactive Energy | 0 | 0~9999999.9
17033 | 4289
17034 | 428A |  | Export Reactive Energy | 0 | 0~9999999.9
17035 | 428B
17036 | 428C | Last 6th month Energy (Off-peak） | Total Active Energy | 0 | 0~9999999.9
17037 | 428D
17038 | 428E |  | Import Active Energy | 0 | 0~9999999.9
17039 | 428F
17040 | 4290 |  | Export Active Energy | 0 | 0~9999999.9
17041 | 4291
17042 | 4292 |  | Total Reactive Energy | 0 | 0~9999999.9
17043 | 4293
17044 | 4294 |  | Import Reactive Energy | 0 | 0~9999999.9
17045 | 4295
17046 | 4296 |  | Export Reactive Energy | 0 | 0~9999999.9
17047 | 4297
17048 | 4298 | Last 6th month Energy (shoulder) | Total Active Energy | 0 | 0~9999999.9
17049 | 4299
17050 | 429A |  | Import Active Energy | 0 | 0~9999999.9
17051 | 429B
17052 | 429C |  | Export Active Energy | 0 | 0~9999999.9
17053 | 429D
17054 | 429E |  | Total Reactive Energy | 0 | 0~9999999.9
17055 | 429F
17056 | 42A0 |  | Import Reactive Energy | 0 | 0~9999999.9
17057 | 42A1
17058 | 42A2 |  | Export Reactive Energy | 0 | 0~9999999.9
17059 | 42A3
17060 | 42A4 | Last 7th month Energy (Total） | Total Active Energy | 0 | 0~9999999.9
17061 | 42A5
17062 | 42A6 |  | Import Active Energy | 0 | 0~9999999.9
17063 | 42A7
17064 | 42A8 |  | Export Active Energy | 0 | 0~9999999.9
17065 | 42A9
17066 | 42AA |  | Total Reactive Energy | 0 | 0~9999999.9
17067 | 42AB
17068 | 42AC |  | Import Reactive Energy | 0 | 0~9999999.9
17069 | 42AD
17070 | 42AE |  | Export Reactive Energy | 0 | 0~9999999.9
17071 | 42AF
17072 | 42B0 | Last 7th month Energy (Sharp） | Total Active Energy | 0 | 0~9999999.9
17073 | 42B1
17074 | 42B2 |  | Import Active Energy | 0 | 0~9999999.9
17075 | 42B3
17076 | 42B4 |  | Export Active Energy | 0 | 0~9999999.9
17077 | 42B5
17078 | 42B6 |  | Total Reactive Energy | 0 | 0~9999999.9
17079 | 42B7
17080 | 42B8 |  | Import Reactive Energy | 0 | 0~9999999.9
17081 | 42B9
17082 | 42BA |  | Export Reactive Energy | 0 | 0~9999999.9
17083 | 42BB
17084 | 42BC | Last 7th month Energy (Peak） | Total Active Energy | 0 | 0~9999999.9
17085 | 42BD
17086 | 42BE |  | Import Active Energy | 0 | 0~9999999.9
17087 | 42BF
17088 | 42C0 |  | Export Active Energy | 0 | 0~9999999.9
17089 | 42C1
17090 | 42C2 |  | Total Reactive Energy | 0 | 0~9999999.9
17091 | 42C3
17092 | 42C4 |  | Import Reactive Energy | 0 | 0~9999999.9
17093 | 42C5
17094 | 42C6 |  | Export Reactive Energy | 0 | 0~9999999.9
17095 | 42C7
17096 | 42C8 | Last 7th month Energy (Off-peak） | Total Active Energy | 0 | 0~9999999.9
17097 | 42C9
17098 | 42CA |  | Import Active Energy | 0 | 0~9999999.9
17099 | 42CB
17100 | 42CC |  | Export Active Energy | 0 | 0~9999999.9
17101 | 42CD
17102 | 42CE |  | Total Reactive Energy | 0 | 0~9999999.9
17103 | 42CF
17104 | 42D0 |  | Import Reactive Energy | 0 | 0~9999999.9
17105 | 42D1
17106 | 42D2 |  | Export Reactive Energy | 0 | 0~9999999.9
17107 | 42D3
17108 | 42D4 | Last 7th month Energy (shoulder) | Total Active Energy | 0 | 0~9999999.9
17109 | 42D5
17110 | 42D6 |  | Import Active Energy | 0 | 0~9999999.9
17111 | 42D7
17112 | 42D8 |  | Export Active Energy | 0 | 0~9999999.9
17113 | 42D9
17114 | 42DA |  | Total Reactive Energy | 0 | 0~9999999.9
17115 | 42DB
17116 | 42DC |  | Import Reactive Energy | 0 | 0~9999999.9
17117 | 42DD
17118 | 42DE |  | Export Reactive Energy | 0 | 0~9999999.9
17119 | 42DF
17120 | 42 | Last 8th month Energy (Total） | Total Active Energy | 0 | 0~9999999.9
17121 | 420
17122 | 4200 |  | Import Active Energy | 0 | 0~9999999.9
17123 | 42000
17124 | 420000 |  | Export Active Energy | 0 | 0~9999999.9
17125 | 4200000
17126 | 42000000 |  | Total Reactive Energy | 0 | 0~9999999.9
17127 | 420000000
17128 | 4200000000 |  | Import Reactive Energy | 0 | 0~9999999.9
17129 | 42000000000
17130 | 42EA |  | Export Reactive Energy | 0 | 0~9999999.9
17131 | 42EB
17132 | 42EC | Last 8th month Energy (Sharp） | Total Active Energy | 0 | 0~9999999.9
17133 | 42ED
17134 | 42EE |  | Import Active Energy | 0 | 0~9999999.9
17135 | 42EF
17136 | 42F0 |  | Export Active Energy | 0 | 0~9999999.9
17137 | 42F1
17138 | 42F2 |  | Total Reactive Energy | 0 | 0~9999999.9
17139 | 42F3
17140 | 42F4 |  | Import Reactive Energy | 0 | 0~9999999.9
17141 | 42F5
17142 | 42F6 |  | Export Reactive Energy | 0 | 0~9999999.9
17143 | 42F7
17144 | 42F8 | Last 8th month Energy (Peak） | Total Active Energy | 0 | 0~9999999.9
17145 | 42F9
17146 | 42FA |  | Import Active Energy | 0 | 0~9999999.9
17147 | 42FB
17148 | 42FC |  | Export Active Energy | 0 | 0~9999999.9
17149 | 42FD
17150 | 42FE |  | Total Reactive Energy | 0 | 0~9999999.9
17151 | 42FF
17152 | 4300 |  | Import Reactive Energy | 0 | 0~9999999.9
17153 | 4301
17154 | 4302 |  | Export Reactive Energy | 0 | 0~9999999.9
17155 | 4303
17156 | 4304 | Last 8th month Energy (Off-peak） | Total Active Energy | 0 | 0~9999999.9
17157 | 4305
17158 | 4306 |  | Import Active Energy | 0 | 0~9999999.9
17159 | 4307
17160 | 4308 |  | Export Active Energy | 0 | 0~9999999.9
17161 | 4309
17162 | 430A |  | Total Reactive Energy | 0 | 0~9999999.9
17163 | 430B
17164 | 430C |  | Import Reactive Energy | 0 | 0~9999999.9
17165 | 430D
17166 | 430E |  | Export Reactive Energy | 0 | 0~9999999.9
17167 | 430F
17168 | 4310 | Last 8th month Energy (shoulder) | Total Active Energy | 0 | 0~9999999.9
17169 | 4311
17170 | 4312 |  | Import Active Energy | 0 | 0~9999999.9
17171 | 4313
17172 | 4314 |  | Export Active Energy | 0 | 0~9999999.9
17173 | 4315
17174 | 4316 |  | Total Reactive Energy | 0 | 0~9999999.9
17175 | 4317
17176 | 4318 |  | Import Reactive Energy | 0 | 0~9999999.9
17177 | 4319
17178 | 431A |  | Export Reactive Energy | 0 | 0~9999999.9
17179 | 431B
17180 | 431C | Last 9th month Energy (Total） | Total Active Energy | 0 | 0~9999999.9
17181 | 431D
17182 | 431E |  | Import Active Energy | 0 | 0~9999999.9
17183 | 431F
17184 | 4320 |  | Export Active Energy | 0 | 0~9999999.9
17185 | 4321
17186 | 4322 |  | Total Reactive Energy | 0 | 0~9999999.9
17187 | 4323
17188 | 4324 |  | Import Reactive Energy | 0 | 0~9999999.9
17189 | 4325
17190 | 4326 |  | Export Reactive Energy | 0 | 0~9999999.9
17191 | 4327
17192 | 4328 | Last 9th month Energy (Sharp） | Total Active Energy | 0 | 0~9999999.9
17193 | 4329
17194 | 432A |  | Import Active Energy | 0 | 0~9999999.9
17195 | 432B
17196 | 432C |  | Export Active Energy | 0 | 0~9999999.9
17197 | 432D
17198 | 432E |  | Total Reactive Energy | 0 | 0~9999999.9
17199 | 432F
17200 | 4330 |  | Import Reactive Energy | 0 | 0~9999999.9
17201 | 4331
17202 | 4332 |  | Export Reactive Energy | 0 | 0~9999999.9
17203 | 4333
17204 | 4334 | Last 9th month Energy (Peak） | Total Active Energy | 0 | 0~9999999.9
17205 | 4335
17206 | 4336 |  | Import Active Energy | 0 | 0~9999999.9
17207 | 4337
17208 | 4338 |  | Export Active Energy | 0 | 0~9999999.9
17209 | 4339
17210 | 433A |  | Total Reactive Energy | 0 | 0~9999999.9
17211 | 433B
17212 | 433C |  | Import Reactive Energy | 0 | 0~9999999.9
17213 | 433D
17214 | 433E |  | Export Reactive Energy | 0 | 0~9999999.9
17215 | 433F
17216 | 4340 | Last 9th month Energy (Off-peak） | Total Active Energy | 0 | 0~9999999.9
17217 | 4341
17218 | 4342 |  | Import Active Energy | 0 | 0~9999999.9
17219 | 4343
17220 | 4344 |  | Export Active Energy | 0 | 0~9999999.9
17221 | 4345
17222 | 4346 |  | Total Reactive Energy | 0 | 0~9999999.9
17223 | 4347
17224 | 4348 |  | Import Reactive Energy | 0 | 0~9999999.9
17225 | 4349
17226 | 434A |  | Export Reactive Energy | 0 | 0~9999999.9
17227 | 434B
17228 | 434C | Last 9th month Energy (shoulder) | Total Active Energy | 0 | 0~9999999.9
17229 | 434D
17230 | 434E |  | Import Active Energy | 0 | 0~9999999.9
17231 | 434F
17232 | 4350 |  | Export Active Energy | 0 | 0~9999999.9
17233 | 4351
17234 | 4352 |  | Total Reactive Energy | 0 | 0~9999999.9
17235 | 4353
17236 | 4354 |  | Import Reactive Energy | 0 | 0~9999999.9
17237 | 4355
17238 | 4356 |  | Export Reactive Energy | 0 | 0~9999999.9
17239 | 4357
17240 | 4358 | Last 10th month Energy (Total） | Total Active Energy | 0 | 0~9999999.9
17241 | 4359
17242 | 435A |  | Import Active Energy | 0 | 0~9999999.9
17243 | 435B
17244 | 435C |  | Export Active Energy | 0 | 0~9999999.9
17245 | 435D
17246 | 435E |  | Total Reactive Energy | 0 | 0~9999999.9
17247 | 435F
17248 | 4360 |  | Import Reactive Energy | 0 | 0~9999999.9
17249 | 4361
17250 | 4362 |  | Export Reactive Energy | 0 | 0~9999999.9
17251 | 4363
17252 | 4364 | Last 10th month Energy (Sharp） | Total Active Energy | 0 | 0~9999999.9
17253 | 4365
17254 | 4366 |  | Import Active Energy | 0 | 0~9999999.9
17255 | 4367
17256 | 4368 |  | Export Active Energy | 0 | 0~9999999.9
17257 | 4369
17258 | 436A |  | Total Reactive Energy | 0 | 0~9999999.9
17259 | 436B
17260 | 436C |  | Import Reactive Energy | 0 | 0~9999999.9
17261 | 436D
17262 | 436E |  | Export Reactive Energy | 0 | 0~9999999.9
17263 | 436F
17264 | 4370 | Last 10th month Energy (Peak） | Total Active Energy | 0 | 0~9999999.9
17265 | 4371
17266 | 4372 |  | Import Active Energy | 0 | 0~9999999.9
17267 | 4373
17268 | 4374 |  | Export Active Energy | 0 | 0~9999999.9
17269 | 4375
17270 | 4376 |  | Total Reactive Energy | 0 | 0~9999999.9
17271 | 4377
17272 | 4378 |  | Import Reactive Energy | 0 | 0~9999999.9
17273 | 4379
17274 | 437A |  | Export Reactive Energy | 0 | 0~9999999.9
17275 | 437B
17276 | 437C | Last 10th month Energy (Off-peak） | Total Active Energy | 0 | 0~9999999.9
17277 | 437D
17278 | 437E |  | Import Active Energy | 0 | 0~9999999.9
17279 | 437F
17280 | 4380 |  | Export Active Energy | 0 | 0~9999999.9
17281 | 4381
17282 | 4382 |  | Total Reactive Energy | 0 | 0~9999999.9
17283 | 4383
17284 | 4384 |  | Import Reactive Energy | 0 | 0~9999999.9
17285 | 4385
17286 | 4386 |  | Export Reactive Energy | 0 | 0~9999999.9
17287 | 4387
17288 | 4388 | Last 10th month Energy (shoulder) | Total Active Energy | 0 | 0~9999999.9
17289 | 4389
17290 | 438A |  | Import Active Energy | 0 | 0~9999999.9
17291 | 438B
17292 | 438C |  | Export Active Energy | 0 | 0~9999999.9
17293 | 438D
17294 | 438E |  | Total Reactive Energy | 0 | 0~9999999.9
17295 | 438F
17296 | 4390 |  | Import Reactive Energy | 0 | 0~9999999.9
17297 | 4391
17298 | 4392 |  | Export Reactive Energy | 0 | 0~9999999.9
17299 | 4393
17300 | 4394 | Last 11th month Energy (Total） | Total Active Energy | 0 | 0~9999999.9
17301 | 4395
17302 | 4396 |  | Import Active Energy | 0 | 0~9999999.9
17303 | 4397
17304 | 4398 |  | Export Active Energy | 0 | 0~9999999.9
17305 | 4399
17306 | 439A |  | Total Reactive Energy | 0 | 0~9999999.9
17307 | 439B
17308 | 439C |  | Import Reactive Energy | 0 | 0~9999999.9
17309 | 439D
17310 | 439E |  | Export Reactive Energy | 0 | 0~9999999.9
17311 | 439F
17312 | 43A0 | Last 11th month Energy (Sharp） | Total Active Energy | 0 | 0~9999999.9
17313 | 43A1
17314 | 43A2 |  | Import Active Energy | 0 | 0~9999999.9
17315 | 43A3
17316 | 43A4 |  | Export Active Energy | 0 | 0~9999999.9
17317 | 43A5
17318 | 43A6 |  | Total Reactive Energy | 0 | 0~9999999.9
17319 | 43A7
17320 | 43A8 |  | Import Reactive Energy | 0 | 0~9999999.9
17321 | 43A9
17322 | 43AA |  | Export Reactive Energy | 0 | 0~9999999.9
17323 | 43AB
17324 | 43AC | Last 11th month Energy (Peak） | Total Active Energy | 0 | 0~9999999.9
17325 | 43AD
17326 | 43AE |  | Import Active Energy | 0 | 0~9999999.9
17327 | 43AF
17328 | 43B0 |  | Export Active Energy | 0 | 0~9999999.9
17329 | 43B1
17330 | 43B2 |  | Total Reactive Energy | 0 | 0~9999999.9
17331 | 43B3
17332 | 43B4 |  | Import Reactive Energy | 0 | 0~9999999.9
17333 | 43B5
17334 | 43B6 |  | Export Reactive Energy | 0 | 0~9999999.9
17335 | 43B7
17336 | 43B8 | Last 11th month Energy (Off-peak） | Total Active Energy | 0 | 0~9999999.9
17337 | 43B9
17338 | 43BA |  | Import Active Energy | 0 | 0~9999999.9
17339 | 43BB
17340 | 43BC |  | Export Active Energy | 0 | 0~9999999.9
17341 | 43BD
17342 | 43BE |  | Total Reactive Energy | 0 | 0~9999999.9
17343 | 43BF
17344 | 43C0 |  | Import Reactive Energy | 0 | 0~9999999.9
17345 | 43C1
17346 | 43C2 |  | Export Reactive Energy | 0 | 0~9999999.9
17347 | 43C3
17348 | 43C4 | Last 11th month Energy (shoulder) | Total Active Energy | 0 | 0~9999999.9
17349 | 43C5
17350 | 43C6 |  | Import Active Energy | 0 | 0~9999999.9
17351 | 43C7
17352 | 43C8 |  | Export Active Energy | 0 | 0~9999999.9
17353 | 43C9
17354 | 43CA |  | Total Reactive Energy | 0 | 0~9999999.9
17355 | 43CB
17356 | 43CC |  | Import Reactive Energy | 0 | 0~9999999.9
17357 | 43CD
17358 | 43CE |  | Export Reactive Energy | 0 | 0~9999999.9
17359 | 43CF
17360 | 43D0 | 上一结算日累计电能（总电能） | Total Active Energy | 0 | 0~9999999.9
17361 | 43D1
17362 | 43D2 |  | Import Active Energy | 0 | 0~9999999.9
17363 | 43D3
17364 | 43D4 |  | Export Active Energy | 0 | 0~9999999.9
17365 | 43D5
17366 | 43D6 |  | Total Reactive Energy | 0 | 0~9999999.9
17367 | 43D7
17368 | 43D8 |  | Import Reactive Energy | 0 | 0~9999999.9
17369 | 43D9
17370 | 43DA |  | Export Reactive Energy | 0 | 0~9999999.9
17371 | 43DB
17372 | 43DC | 上一结算日累计电能（尖时段电能） | Total Active Energy | 0 | 0~9999999.9
17373 | 43DD
17374 | 43DE |  | Import Active Energy | 0 | 0~9999999.9
17375 | 43DF
17376 | 43 |  | Export Active Energy | 0 | 0~9999999.9
17377 | 430
17378 | 4300 |  | Total Reactive Energy | 0 | 0~9999999.9
17379 | 43000
17380 | 430000 |  | Import Reactive Energy | 0 | 0~9999999.9
17381 | 4300000
17382 | 43000000 |  | Export Reactive Energy | 0 | 0~9999999.9
17383 | 430000000
17384 | 4300000000 | 上一结算日累计电能（峰时段电能） | Total Active Energy | 0 | 0~9999999.9
17385 | 43000000000
17386 | 43EA |  | Import Active Energy | 0 | 0~9999999.9
17387 | 43EB
17388 | 43EC |  | Export Active Energy | 0 | 0~9999999.9
17389 | 43ED
17390 | 43EE |  | Total Reactive Energy | 0 | 0~9999999.9
17391 | 43EF
17392 | 43F0 |  | Import Reactive Energy | 0 | 0~9999999.9
17393 | 43F1
17394 | 43F2 |  | Export Reactive Energy | 0 | 0~9999999.9
17395 | 43F3
17396 | 43F4 | 上一结算日累计电能（平时段电能） | Total Active Energy | 0 | 0~9999999.9
17397 | 43F5
17398 | 43F6 |  | Import Active Energy | 0 | 0~9999999.9
17399 | 43F7
17400 | 43F8 |  | Export Active Energy | 0 | 0~9999999.9
17401 | 43F9
17402 | 43FA |  | Total Reactive Energy | 0 | 0~9999999.9
17403 | 43FB
17404 | 43FC |  | Import Reactive Energy | 0 | 0~9999999.9
17405 | 43FD
17406 | 43FE |  | Export Reactive Energy | 0 | 0~9999999.9
17407 | 43FF
17408 | 4400 | 上一结算日累计电能（平时段电能） | Total Active Energy | 0 | 0~9999999.9
17409 | 4401
17410 | 4402 |  | Import Active Energy | 0 | 0~9999999.9
17411 | 4403
17412 | 4404 |  | Export Active Energy | 0 | 0~9999999.9
17413 | 4405
17414 | 4406 |  | Total Reactive Energy | 0 | 0~9999999.9
17415 | 4407
17416 | 4408 |  | Import Reactive Energy | 0 | 0~9999999.9
17417 | 4409
17418 | 440A |  | Export Reactive Energy | 0 | 0~9999999.9
17419 | 440B

## Formula
Formulas Between Real Values and Modbus Registers' Values(Rx：Modbus Registers' Values)
Parameters | Formula | Unit
Voltage: Ua,Ub,Uc,Uab,Ubc,Uca,Un | U＝Rx×100 | V
Current: Ia,Ib,Ic，In | I＝Rx×1000 | A
Active Power: Pa, Pb, Pc, Psum | P＝Rx/1000 | kW
Reactive Power: Qa, Qb，Qc，Qsum | Q＝Rx/1000 | kVar
Apparent Power: Ssum | S＝Rx/1000 | kVA
Energy:E | E＝(65536×RxH+RxL)/10 | kWh
Power Factor: PFa，PFb，PFc，Pfsum | PF＝Rx/1000
Frequency: F | F＝Rx/100 | Hz
Unbalance Factor : U_unbl,I_unbl | Unbl=(Rx/100)×100%
Harmonic Content | Unbl=(Rx/100)×100% | %