## Basic Parameter
Basically Measured Parameters Zone （Function Code 03 only read）
Address |  | Circuit | Parameters | Data Fornat | Value Range | Remark
(Decimal) | (hexadecimal)
0000 | 0000 | voltage | Common Voltage | xxx.xxx | 0～1000 | hexadecimal
0001 | 0001
0002 | 0002 |  | Reserved
...
0013 | 000D
0014 | 000E |  | Current of loop 1 | xxxx.xxxx | -32768～32767 | hexadecimal
0015 | 000F
0016 | 0010 |  | Current of loop 2 | xxxx.xxxx | -32768～32767 | hexadecimal
0017 | 0011
0018 | 0012 |  | Current of loop 3 | xxxx.xxxx | -32768～32767 | hexadecimal
0019 | 0013 |  |  |  | -32768～32767
0020 | 0014 |  | Current of loop 4 | xxxx.xxxx | -32768～32767 | hexadecimal
0021 | 0015
0022 | 0016 |  | Reserved
...
0025 | 0019
0026 | 001A |  | Total Active Power | xxxx.xxxx | -1000～1000 | hexadecimal
0027 | 001B |  | Phase A Power Factor | magnifying 1000 times
0028 | 001C |  | Active Power of loop 1 | xxxx.xxxx | -1000～1000 | hexadecimal
0029 | 001D |  |  |  | -1000～1000
0030 | 001E |  | Active Power of loop 2 | xxxx.xxxx | -1000～1000 | hexadecimal
0031 | 001F | Loop 2 |  |  | -32768～32767
0032 | 0020 |  | Active Power of loop 3 | xxxx.xxxx | -1000～1000 | hexadecimal
0033 | 0021
0034 | 0022 |  | Active Power of loop 4 | xxxx.xxxx | -1000～1000 | hexadecimal
0035 | 0023
0036 | 0024 |  | Reserved
...
0039 | 0027
0040 | 0028 |  | Total Import Active Energy | xxxxxx.xx | -32768～32767 | hexadecimal
0041 | 0029
0042 | 002A |  | Import Active Energy of loop 1 | xxxxxx.xx | -32768～32767 | hexadecimal
0043 | 002B
0044 | 002C |  | Import Active Energy of loop 2 | xxxxxx.xx | -32768～32767 | hexadecimal
0045 | 002D
0046 | 002E |  | Import Active Energy of loop 3 | xxxxxx.xx | -32768～32767 | hexadecimal
0047 | 002F
0048 | 0030 |  | Import Active Energy of loop 4 | xxxxxx.xx | -32768～32767 | hexadecimal
0049 | 0031
0050 | 0032 |  | Reserved
...
0053 | 0035
0054 | 0036 | Loop 3 | Total Export Active Energy | xxxxxx.xx | -32768～32767 | hexadecimal
0055 | 0037
0056 | 0038 |  | Export Active Energy of loop 1 | xxxxxx.xx | -32768～32767 | hexadecimal
0057 | 0039
0058 | 003A |  | Export Active Energy of loop 2 | xxxxxx.xx | -32768～32767 | hexadecimal
0059 | 003B
0060 | 003C |  | Export Active Energy of loop 3 | xxxxxx.xx | -32768～32767 | hexadecimal
0061 | 003D
0062 | 003E |  | Export Active Energy of loop 4 | xxxxxx.xx | -32768～32767 | hexadecimal
0063 | 003F

## Basic Set
Add (Decimal) | Address (Hexadecimal) | Parameter | Data Fornat | Type | Default Value | Value Range
0000 | 0000 | Voltage | xxx.xxx | Read | 0
0001 | 0001
... |  | Reserved
0014 | 000E | Current for the 1st loop | xxxx.xxxx | Read
0015 | 000F
0016 | 0010 | Current for the 2st loop | xxxx.xxxx | Read
0017 | 0011
0018 | 0012 | Current for the 3st loop | xxxx.xxxx | Read
0019 | 0013
0020 | 0014 | Current for the 4st loop | xxxx.xxxx | Read
0021 | 0015
... |  | Reserved
0028 | 000C | Active Power for the 1st loop | xxxx.xxxx | Read
0029 | 001D
0030 | 001E | Active Power for the 2st loop | xxxx.xxxx | Read
0031 | 001F
0032 | 0020 | Active Power for the 3st loop | xxxx.xxxx | Read
0033 | 0021
0034 | 0022 | Active Power for the 4st loop | xxxx.xxxx | Read
0035 | 0023
0040 | 0028 | Total Import Active Energy | xxxxxx.xx | Read
0041 | 0029
0042 | 002A | Import Active Energy for the 1st loop | xxxxxx.xx | Read
0043 | 002B
0044 | 002C | Import Active Energy for the 2st loop | xxxxxx.xx | Read
0045 | 002D
0046 | 002E | Import Active Energy for the 3st loop | xxxxxx.xx | Read
0047 | 002F
0048 | 0030 | Import Active Energy for the 4st loop | xxxxxx.xx | Read
0049 | 0031
... |  | Reserved
0054 | 0036 | Total Export Active Energy | xxxxxx.xx | Read
0055 | 0037
0056 | 0038 | Export Active Energy for the 1st loop | xxxxxx.xx | Read
0057 | 0039
0058 | 003A | Export Active Energy for the 2st loop | xxxxxx.xx | Read
0059 | 003B
0060 | 003C | Export Active Energy for the 3st loop | xxxxxx.xx | Read
0061 | 003D
0062 | 003E | Export Active Energy for the 4st loop | xxxxxx.xx | Read
0063 | 003F
... |  | Reserved
768 | 0300 | Communication address | xxx | Read/Write | 1 | 1～247
772 | 0304 | Baud Rate | 0x08： 1200 0x10： 2400 0x20： 4800 0x40： 9600 0x80： 19200 | Read/Write | 2400 | 1200~19200
773 | 0305 | Parity Bit | 0x00：8N1 0x01：8O1 0x02：8E1 | Read/Write | 8N1
1280 | 0500 | Year | xx | Read/Write | 0 | 0~99
1281 | 0501 | Month | xx | Read/Write | 1 | 1~12
1282 | 0502 | Day | xx | Read/Write | 1 | 1~31
1283 | 0503 | Hour | xx | Read/Write | 1 | 0~23
1284 | 0504 | Minite | xx | Read/Write | 1 | 0∼59
1285 | 0505 | Second | xx | Read/Write | 1 | 0∼59
65535 | FFFF | Zero Shielding | Xxxx, unit:‰ | Read/Write
1361 | 0551 | Energy Clear | 0 | Write | 1 | 0