## Basic Setting
Parameter Setting Zone
No. | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
2 | 8192 | 2000 | 03 Read 06/10 Write |  | Wiring Mode | Unsigned 16-bit | 0 | 0～2 | —— | 0：3P4W 1：3P3W 2CT 2：3P3W 3CT 3：Single Phase 3 Circuits
3 | 8193 | 2001 | 03 Read 06/10 Write |  | Secondary Side Voltage | Unsigned 16-bit | 0 | 0～1 | -- | 0:220V L-N/380V L-L 1:57.7V L-N/100V L-L
4 | 8194 | 2002 | 03 Read 06/10 Write |  | PT | Unsigned 16-bit | 1 | 1～5500 | ——
5 | 8195 | 2003 | 03 Read 06/10 Write |  | CT | Unsigned 16-bit | 1 | 1～50000 | ——
1 | 8240 | 2030 | 03 Read 06/10 Write | Demand | Sliding Window | Unsigned 16-bit | 0 | 0～15 | ——
2 | 8241 | 2031 | 03 Read 06/10 Write |  | Cycle | Unsigned 16-bit | 0 | 0～15 | ——
1 | 8288 | 2060 | 03 Read 06/10 Write | RS485 Communicati on settings | Meter Address | Unsigned 16-bit | 1 | 1～247 | ——
2 | 8289 | 2061 | 03 Read 06/10 Write |  | Baud Rate | Unsigned 16-bit | 3 | 0～3 | —— | 0:1200,1:2400, 2:4800,3:9600
3 | 8290 | 2062 | 03 Read 06/10 Write |  | Parity | Unsigned 16-bit | 0 | 0～2 | —— | 0:8N1 1:8E1 2:8O1
LORA Parameter Setting
No. | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
1 | 24576 | 6000 | 03 Read 06/10 Write | LORA Parameter | Channel No. | Unsigned 16-bit | 0 | 0-31 | -- | 1-32
2 | 24577 | 6001 | 03 Read 06/10 Write |  | Speed Rate | Unsigned 16-bit | 0 | 0x00-0x60 | -- | 0x00:62.5kbps 0x10:37.5kbps 0x20:21.8kbps 0x30:12.5kbps 0x40:7.0kbps 0x50:3.9kbps 0x60:2.1kbps
3 | 24578 | 6002 | 03 Read 06/10 Write |  | Power | Unsigned 16-bit | 0 | 0-7 | -- | 000:22dbm 001:20dbm 010:17dbm 011:14dbm 100:11dbm 101:8dbm 110:5dbm 111:2dbm
4 | 24579 | 6003 | 03 Read 06/10 Write |  | RF Band | Unsigned 16-bit | 0 | 0-3 | -- | 00:433MHz 01:470MHz 10:480MHz 11:500MHz
5 | 24580 | 6004 | 03 Read 06/10 Write |  | Network ID | Unsigned 16-bit | 0 | 0x00 0x00 0x00 |  | low 3 bytes
6 | 24581 | 6005 | 03 Read 06/10 Write |  |  | Unsigned 16-bit |  |  | --
7 | 24582 | 6006 | 03 Read |  | MAC ID | Unsigned 16-bit |  |  | --
8 | 24583 | 6007 | 03 Read |  |  | Unsigned 16-bit |  |  | --
9 | 24584 | 6008 | 03 Read |  |  | Unsigned 16-bit |  |  | --
Reserved
10 | 24588 | 600C | 03 Read |  | Unique ID | Unsigned 16-bit |  |  | --
11 | 24589 | 600D | 03 Read |  |  | Unsigned 16-bit |  |  | --
12 | 24590 | 600E | 03 Read |  |  | Unsigned 16-bit |  |  | --
Password Setting Zone
No. | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
1 | 61600 | F0A0 | 06 Write | Password |  | Unsigned 16-bit | 0 | 0, 2～9999 | —— | cannot be set as 1
Real-time Clock Zone
No, | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
1 | 12800 | 3200 | 03 Read 06/10 Write | Time | Year | Unsigned 16-bit | 2000 | 2000～2099 | Year
2 | 12801 | 3201 | 03 Read 06/10 Write |  | Month | Unsigned 16-bit | 1 | 1～12 | Month
3 | 12802 | 3202 | 03 Read 06/10 Write |  | Date | Unsigned 16-bit | 1 | 1～31 | Date
4 | 12803 | 3203 | 03 Read 06/10 Write |  | Hour | Unsigned 16-bit | 0 | 0～23 | Hour
5 | 12804 | 3204 | 03 Read 06/10 Write |  | Minite | Unsigned 16-bit | 0 | 0～59 | Minite
6 | 12805 | 3205 | 03 Read 06/10 Write |  | Second | Unsigned 16-bit | 0 | 0～59 | Second
7 | 12806 | 3206 | 03 Read 06/10 Write |  | millisecond | Unsigned 16-bit | 0 | 0～999 | millisecond

## Measuring Parameter(Primary)
Basic Measured Parameters Zone--Primary Side
No. | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
1 | 5376 | 1500 | 03/04 read | Phase Voltage | phase A voltage | Unsigned 32-bit | 0 | 0～4294967295 | V | magnifying 100 times
2 | 5377 | 1501 | 03/04 read
3 | 5378 | 1502 | 03/04 read |  | phase B voltage | Unsigned 32-bit | 0 | 0～4294967295 | V | magnifying 100 times
4 | 5379 | 1503 | 03/04 read
5 | 5380 | 1504 | 03/04 read |  | phase C voltage | Unsigned 32-bit | 0 | 0～4294967295 | V | magnifying 100 times
6 | 5381 | 1505 | 03/04 read
7 | 5382 | 1506 | 03/04 read |  | phase voltage mean value | Unsigned 32-bit | 0 | 0～4294967295 | V | magnifying 100 times
8 | 5383 | 1507 | 03/04 read
9 | 5384 | 1508 | 03/04 read |  | zero sequence voltage | Unsigned 32-bit | 0 | 0～4294967295 | V | magnifying 100 times
10 | 5385 | 1509 | 03/04 read
11 | 5386 | 150A | 03/04 read | Line Voltage | line voltage(A-B) | Unsigned 32-bit | 0 | 0～4294967295 | V | magnifying 100 times
12 | 5387 | 150B | 03/04 read
13 | 5388 | 150C | 03/04 read |  | line voltage(B-C) | Unsigned 32-bit | 0 | 0～4294967295 | V | magnifying 100 times
14 | 5389 | 150D | 03/04 read
15 | 5390 | 150E | 03/04 read |  | line voltage(C-A) | Unsigned 32-bit | 0 | 0～4294967295 | V | magnifying 100 times
16 | 5391 | 150F | 03/04 read
17 | 5392 | 1510 | 03/04 read |  | line voltage mean value | Unsigned 32-bit | 0 | 0～4294967295 | V | magnifying 100 times
18 | 5393 | 1511 | 03/04 read
19 | 5394 | 1512 | 03/04 read | Current | Current of phase A | Unsigned 32-bit | 0 | 0～4294967295 | A | magnifying 1000 times
20 | 5395 | 1513 | 03/04 read
21 | 5396 | 1514 | 03/04 read |  | Current of phase B | Unsigned 32-bit | 0 | 0～4294967295 | A | magnifying 1000 times
22 | 5397 | 1515 | 03/04 read
23 | 5398 | 1516 | 03/04 read |  | Current of phase C | Unsigned 32-bit | 0 | 0～4294967295 | A | magnifying 1000 times
24 | 5399 | 1517 | 03/04 read
25 | 5400 | 1518 | 03/04 read |  | Current mean value | Unsigned 32-bit | 0 | 0～4294967295 | A | magnifying 1000 times
26 | 5401 | 1519 | 03/04 read
27 | 5402 | 151A | 03/04 read |  | zero sequence current | Unsigned 32-bit | 0 | 0～4294967295 | A | magnifying 1000 times
28 | 5403 | 151B | 03/04 read
29 | 5404 | 151C | 03/04 read | Active Power | active power of phase A | Signed 32-bit | 0 | -2147483648～2147483647 | kW | magnifying 1000 times
30 | 5405 | 151D | 03/04 read
31 | 5406 | 151E | 03/04 read |  | active power of phase B | Signed 32-bit | 0 | -2147483648～2147483647 | kW | magnifying 1000 times
32 | 5407 | 151F | 03/04 read
33 | 5408 | 1520 | 03/04 read |  | active power of phase C | Signed 32-bit | 0 | -2147483648～2147483647 | kW | magnifying 1000 times
34 | 5409 | 1521 | 03/04 read
35 | 5410 | 1522 | 03/04 read |  | total three-phase reactive power | Signed 32-bit | 0 | -2147483648～2147483647 | kW | magnifying 1000 times
36 | 5411 | 1523 | 03/04 read
37 | 5412 | 1524 | 03/04 read | Reactive Power | reactive power of phase A | Signed 32-bit | 0 | -2147483648～2147483647 | kvar | magnifying 1000 times
38 | 5413 | 1525 | 03/04 read
39 | 5414 | 1526 | 03/04 read |  | reactive power of phase B | Signed 32-bit | 0 | -2147483648～2147483647 | kvar | magnifying 1000 times
40 | 5415 | 1527 | 03/04 read
41 | 5416 | 1528 | 03/04 read |  | reactive power of phase C | Signed 32-bit | 0 | -2147483648～2147483647 | kvar | magnifying 1000 times
42 | 5417 | 1529 | 03/04 read
43 | 5418 | 152A | 03/04 read |  | total three-phase reactive power | Signed 32-bit | 0 | -2147483648～2147483647 | kvar | magnifying 1000 times
44 | 5419 | 152B | 03/04 read
45 | 5420 | 152C | 03/04 read | Apparent Power | apparent power of phase A | Unsigned 32-bit | 0 | 0～4294967295 | kVA | magnifying 1000 times
46 | 5421 | 152D | 03/04 read
47 | 5422 | 152E | 03/04 read |  | apparent power of phase B | Unsigned 32-bit | 0 | 0～4294967295 | kVA | magnifying 1000 times
48 | 5423 | 152F | 03/04 read
49 | 5424 | 1530 | 03/04 read |  | apparent power of phase C | Unsigned 32-bit | 0 | 0～4294967295 | kVA | magnifying 1000 times
50 | 5425 | 1531 | 03/04 read
51 | 5426 | 1532 | 03/04 read |  | total three-phase apparent power | Unsigned 32-bit | 0 | 0～4294967295 | kVA | magnifying 1000 times
52 | 5427 | 1533 | 03/04 read
53 | 5428 | 1534 | 03/04 read | Power Factor | power factor of phase A | Signed 16-bit | 0 | -1000～1000 | —— | magnifying 1000 times
54 | 5429 | 1535 | 03/04 read |  | power factor of phase B | Signed 16-bit | 0 | -1000～1000 | —— | magnifying 1000 times
55 | 5430 | 1536 | 03/04 read |  | power factor of phase C | Signed 16-bit | 0 | -1000～1000 | —— | magnifying 1000 times
56 | 5431 | 1537 | 03/04 read |  | total three-phase power factor | Signed 16-bit | 0 | -1000～1000 | —— | magnifying 1000 times
57 | 5432 | 1538 | 03/04 read | Frequency | Frequency | Unsigned 16-bit | 0 | 0～65535 | Hz | magnifying 100 times
58 | 5433 | 1539 | 03/04 read | Unbalance Factor | Voltage Unbalance Factor | Unsigned 16-bit | 0 | 0～65535 | —— | magnifying 100 times
59 | 5434 | 153A | 03/04 read |  | Current Unbalance Factor | Unsigned 16-bit | 0 | 0～65535 | —— | magnifying 100 times
60 | 5435 | 153B | 03/04 read | Temperature | Temp of Phase A | Signed 16-bit | 0 | -32768～32767 | ℃ | magnifying 10 times
61 | 5436 | 153C | 03/04 read |  | Temp of Phase B | Signed 16-bit | 0 | -32768～32767 | ℃ | magnifying 10 times
62 | 5437 | 153D | 03/04 read |  | Temp of Phase C | Signed 16-bit | 0 | -32768～32767 | ℃ | magnifying 10 times
63 | 5438 | 153E | 03/04 read |  | Temp of Phase N(Environment) | Signed 16-bit | 0 | -32768～32767 | ℃ | magnifying 10 times
64 | 5439 | 153F | 03/04 read | Full wave leakage current | Full wave leakage current | Unsigned 32-bit | 0 | 0～4294967295 | A | magnifying 1000 times
65 | 5440 | 1540 | 03/04 read
66 | 5441 | 1541 | 03/04 read | Fundamental leakage current | Fundamental leakage current | Unsigned 32-bit | 0 | 0～4294967295 | A | magnifying 1000 times
67 | 5442 | 1542 | 03/04 read
68 | 5443 | 1543 | 03/04 read | Reserved
69 | 5444 | 1544 | 03/04 read
70 | 5445 | 1545 | 03/04 read
71 | 5446 | 1546 | 03/04 read
72 | 5447 | 1547 | 03/04 read
73 | 5448 | 1548 | 03/04 read
74 | 5449 | 1549 | 03/04 read
75 | 5450 | 154A | 03/04 read
76 | 5451 | 154B | 03/04 read | phase angle | U-U ab | Unsigned 16-bit |  | 0～359 | 1°
77 | 5452 | 154C | 03/04 read |  | U-U bc | Unsigned 16-bit |  | 0～359 | 1°
78 | 5453 | 154D | 03/04 read |  | U-U ca | Unsigned 16-bit |  | 0～359 | 1°
79 | 5454 | 154E | 03/04 read |  | U-I ab | Unsigned 16-bit |  | 0～359 | 1°
80 | 5455 | 154F | 03/04 read |  | U-I bc | Unsigned 16-bit |  | 0～359 | 1°
81 | 5456 | 1550 | 03/04 read |  | U-I ca | Unsigned 16-bit |  | 0～359 | 1°
82 | 5457 | 1551 | 03/04 read |  | I-I ab | Unsigned 16-bit |  | 0～359 | 1°
83 | 5458 | 1552 | 03/04 read |  | I-I bc | Unsigned 16-bit |  | 0～359 | 1°
84 | 5459 | 1553 | 03/04 read |  | I-I ca | Unsigned 16-bit |  | 0～359 | 1°
85 | 5460 | 1554 | 03/04 read |  | Phase angle normal sign | Unsigned 16-bit |  | 0: abnormal 1: normal
86 | 5461 | 1555 | 03/04 read | Voltage Deviation | Voltage Deviation of Phase A | Unsigned 16-bit
87 | 5462 | 1556 | 03/04 read |  | Voltage Deviation of Phase B | Unsigned 16-bit
88 | 5463 | 1557 | 03/04 read |  | Voltage Deviation of Phase C | Unsigned 16-bit
89 | 5464 | 1558 | 03/04 read |  | Voltage Deviation Mean Value | Unsigned 16-bit
90 | 5465 | 1559 | 03/04 read | DI | DI1 | Unsigned 16-bit | 0 | 0～1 | —— | 0:open 1:close
91 | 5466 | 155A | 03/04 read |  | DI2 | Unsigned 16-bit | 0 | 0～1 | ——
Remark: 1.Primary Voltage Value = Secondary Voltage Value * PT 2.Primary Current Value = Secondary Current Value * CT 3.Primary Power Value = Secondary Power Value * PT * CT

## Energy
Real-time Energy Zone | [10 empty] | The month multi-rate historical Energy Zone
No, | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark | No, | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
1 | 16384 | 4000 | 03/04 Read | Total Real-time Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times | 1 | 17152 | 4300 | 03/04 Read | Total Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
2 | 16385 | 4001 | 03/04 Read | [7 empty] | 2 | 17153 | 4301 | 03/04 Read
3 | 16386 | 4002 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times | 3 | 17154 | 4302 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
4 | 16387 | 4003 | 03/04 Read | [7 empty] | 4 | 17155 | 4303 | 03/04 Read
5 | 16388 | 4004 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times | 5 | 17156 | 4304 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
6 | 16389 | 4005 | 03/04 Read | [7 empty] | 6 | 17157 | 4305 | 03/04 Read
7 | 16390 | 4006 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times | 7 | 17158 | 4306 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
8 | 16391 | 4007 | 03/04 Read | [7 empty] | 8 | 17159 | 4307 | 03/04 Read
9 | 16392 | 4008 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times | 9 | 17160 | 4308 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
10 | 16393 | 4009 | 03/04 Read | [7 empty] | 10 | 17161 | 4309 | 03/04 Read
11 | 16394 | 400A | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times | 11 | 17162 | 430A | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
12 | 16395 | 400B | 03/04 Read | [7 empty] | 12 | 17163 | 430B | 03/04 Read
13 | 16396 | 400C | 03/04 Read | Phase A circuit Real-time Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times | 13 | 17164 | 430C | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
14 | 16397 | 400D | 03/04 Read | [7 empty] | 14 | 17165 | 430D | 03/04 Read
15 | 16398 | 400E | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times | 15 | 17166 | 430E | 03/04 Read |  | 1st quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
16 | 16399 | 400F | 03/04 Read | [7 empty] | 16 | 17167 | 430F | 03/04 Read
17 | 16400 | 4010 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times | 17 | 17168 | 4310 | 03/04 Read |  | 2nd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
18 | 16401 | 4011 | 03/04 Read | [7 empty] | 18 | 17169 | 4311 | 03/04 Read
19 | 16402 | 4012 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times | 19 | 17170 | 4312 | 03/04 Read |  | 3rd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
20 | 16403 | 4013 | 03/04 Read | [7 empty] | 20 | 17171 | 4313 | 03/04 Read
21 | 16404 | 4014 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times | 21 | 17172 | 4314 | 03/04 Read |  | 4th quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
22 | 16405 | 4015 | 03/04 Read | [7 empty] | 22 | 17173 | 4315 | 03/04 Read
23 | 16406 | 4016 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times | 23 | 17174 | 4316 | 03/04 Read | Total Sharp-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
24 | 16407 | 4017 | 03/04 Read | [7 empty] | 24 | 17175 | 4317 | 03/04 Read
25 | 16408 | 4018 | 03/04 Read | Phase B circuit Real-time Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times | 25 | 17176 | 4318 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
26 | 16409 | 4019 | 03/04 Read | [7 empty] | 26 | 17177 | 4319 | 03/04 Read
27 | 16410 | 401A | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times | 27 | 17178 | 431A | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
28 | 16411 | 401B | 03/04 Read | [7 empty] | 28 | 17179 | 431B | 03/04 Read
29 | 16412 | 401C | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times | 29 | 17180 | 431C | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
30 | 16413 | 401D | 03/04 Read | [7 empty] | 30 | 17181 | 431D | 03/04 Read
31 | 16414 | 401E | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times | 31 | 17182 | 431E | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
32 | 16415 | 401F | 03/04 Read | [7 empty] | 32 | 17183 | 431F | 03/04 Read
33 | 16416 | 4020 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times | 33 | 17184 | 4320 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
34 | 16417 | 4021 | 03/04 Read | [7 empty] | 34 | 17185 | 4321 | 03/04 Read
35 | 16418 | 4022 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times | 35 | 17186 | 4322 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
36 | 16419 | 4023 | 03/04 Read | [7 empty] | 36 | 17187 | 4323 | 03/04 Read
37 | 16420 | 4024 | 03/04 Read | Phase C circuit Real-time Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times | 37 | 17188 | 4324 | 03/04 Read | Total Peak-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
38 | 16421 | 4025 | 03/04 Read | [7 empty] | 38 | 17189 | 4325 | 03/04 Read
39 | 16422 | 4026 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times | 39 | 17190 | 4326 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
40 | 16423 | 4027 | 03/04 Read | [7 empty] | 40 | 17191 | 4327 | 03/04 Read
41 | 16424 | 4028 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times | 41 | 17192 | 4328 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
42 | 16425 | 4029 | 03/04 Read | [7 empty] | 42 | 17193 | 4329 | 03/04 Read
43 | 16426 | 402A | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times | 43 | 17194 | 432A | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
44 | 16427 | 402B | 03/04 Read | [7 empty] | 44 | 17195 | 432B | 03/04 Read
45 | 16428 | 402C | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times | 45 | 17196 | 432C | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
46 | 16429 | 402D | 03/04 Read | [7 empty] | 46 | 17197 | 432D | 03/04 Read
47 | 16430 | 402E | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times | 47 | 17198 | 432E | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
48 | 16431 | 402F | 03/04 Read | [7 empty] | 48 | 17199 | 432F | 03/04 Read
[11 empty] | 49 | 17200 | 4330 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 50 | 17201 | 4331 | 03/04 Read
[11 empty] | 51 | 17202 | 4332 | 03/04 Read | Total Flat-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 52 | 17203 | 4333 | 03/04 Read
[11 empty] | 53 | 17204 | 4334 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 54 | 17205 | 4335 | 03/04 Read
[11 empty] | 55 | 17206 | 4336 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 56 | 17207 | 4337 | 03/04 Read
[11 empty] | 57 | 17208 | 4338 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 58 | 17209 | 4339 | 03/04 Read
[11 empty] | 59 | 17210 | 433A | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 60 | 17211 | 433B | 03/04 Read
[11 empty] | 61 | 17212 | 433C | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 62 | 17213 | 433D | 03/04 Read
[11 empty] | 63 | 17214 | 433E | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 64 | 17215 | 433F | 03/04 Read
[11 empty] | 65 | 17216 | 4340 | 03/04 Read | Total Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 66 | 17217 | 4341 | 03/04 Read
[11 empty] | 67 | 17218 | 4342 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 68 | 17219 | 4343 | 03/04 Read
[11 empty] | 69 | 17220 | 4344 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 70 | 17221 | 4345 | 03/04 Read
[11 empty] | 71 | 17222 | 4346 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 72 | 17223 | 4347 | 03/04 Read
[11 empty] | 73 | 17224 | 4348 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 74 | 17225 | 4349 | 03/04 Read
[11 empty] | 75 | 17226 | 434A | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 76 | 17227 | 434B | 03/04 Read
[11 empty] | 77 | 17228 | 434C | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 78 | 17229 | 434D | 03/04 Read
[11 empty] | 79 | 17230 | 434E | 03/04 Read | Total Deep Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 80 | 17231 | 434F | 03/04 Read
[11 empty] | 81 | 17232 | 4350 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 82 | 17233 | 4351 | 03/04 Read
[11 empty] | 83 | 17234 | 4352 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 84 | 17235 | 4353 | 03/04 Read
[11 empty] | 85 | 17236 | 4354 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 86 | 17237 | 4355 | 03/04 Read
[11 empty] | 87 | 17238 | 4356 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 88 | 17239 | 4357 | 03/04 Read
[11 empty] | 89 | 17240 | 4358 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 90 | 17241 | 4359 | 03/04 Read
[11 empty] | 91 | 17242 | 435A | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 92 | 17243 | 435B | 03/04 Read
[11 empty] | 93 | Reserved
94
[11 empty] | 95 | 17246 | 435E | 03/04 Read | Phase A Circuit Total Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 96 | 17247 | 435F | 03/04 Read
[11 empty] | 97 | 17248 | 4360 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 98 | 17249 | 4361 | 03/04 Read
[11 empty] | 99 | 17250 | 4362 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 100 | 17251 | 4363 | 03/04 Read
[11 empty] | 101 | 17252 | 4364 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 102 | 17253 | 4365 | 03/04 Read
[11 empty] | 103 | 17254 | 4366 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 104 | 17255 | 4367 | 03/04 Read
[11 empty] | 105 | 17256 | 4368 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 106 | 17257 | 4369 | 03/04 Read
[11 empty] | 107 | 17258 | 436A | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 108 | 17259 | 436B | 03/04 Read
[11 empty] | 109 | 17260 | 436C | 03/04 Read |  | 1st quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 110 | 17261 | 436D | 03/04 Read
[11 empty] | 111 | 17262 | 436E | 03/04 Read |  | 2nd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 112 | 17263 | 436F | 03/04 Read
[11 empty] | 113 | 17264 | 4370 | 03/04 Read |  | 3rd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 114 | 17265 | 4371 | 03/04 Read
[11 empty] | 115 | 17266 | 4372 | 03/04 Read |  | 4th quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 116 | 17267 | 4373 | 03/04 Read
[11 empty] | 117 | 17268 | 4374 | 03/04 Read | Phase A Circuit Sharp-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 118 | 17269 | 4375 | 03/04 Read
[11 empty] | 119 | 17270 | 4376 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 120 | 17271 | 4377 | 03/04 Read
[11 empty] | 121 | 17272 | 4378 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 122 | 17273 | 4379 | 03/04 Read
[11 empty] | 123 | 17274 | 437A | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 124 | 17275 | 437B | 03/04 Read
[11 empty] | 125 | 17276 | 437C | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 126 | 17277 | 437D | 03/04 Read
[11 empty] | 127 | 17278 | 437E | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 128 | 17279 | 437F | 03/04 Read
[11 empty] | 129 | 17280 | 4380 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 130 | 17281 | 4381 | 03/04 Read
[11 empty] | 131 | 17282 | 4382 | 03/04 Read | Phase A Circuit Peak-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 132 | 17283 | 4383 | 03/04 Read
[11 empty] | 133 | 17284 | 4384 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 134 | 17285 | 4385 | 03/04 Read
[11 empty] | 135 | 17286 | 4386 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 136 | 17287 | 4387 | 03/04 Read
[11 empty] | 137 | 17288 | 4388 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 138 | 17289 | 4389 | 03/04 Read
[11 empty] | 139 | 17290 | 438A | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 140 | 17291 | 438B | 03/04 Read
[11 empty] | 141 | 17292 | 438C | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 142 | 17293 | 438D | 03/04 Read
[11 empty] | 143 | 17294 | 438E | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 144 | 17295 | 438F | 03/04 Read
[11 empty] | 145 | 17296 | 4390 | 03/04 Read | Phase A Circuit Flat-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 146 | 17297 | 4391 | 03/04 Read
[11 empty] | 147 | 17298 | 4392 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 148 | 17299 | 4393 | 03/04 Read
[11 empty] | 149 | 17300 | 4394 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 150 | 17301 | 4395 | 03/04 Read
[11 empty] | 151 | 17302 | 4396 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 152 | 17303 | 4397 | 03/04 Read
[11 empty] | 153 | 17304 | 4398 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 154 | 17305 | 4399 | 03/04 Read
[11 empty] | 155 | 17306 | 439A | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 156 | 17307 | 439B | 03/04 Read
[11 empty] | 157 | 17308 | 439C | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 158 | 17309 | 439D | 03/04 Read
[11 empty] | 159 | 17310 | 439E | 03/04 Read | Phase A Circuit Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 160 | 17311 | 439F | 03/04 Read
[11 empty] | 161 | 17312 | 43A0 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 162 | 17313 | 43A1 | 03/04 Read
[11 empty] | 163 | 17314 | 43A2 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 164 | 17315 | 43A3 | 03/04 Read
[11 empty] | 165 | 17316 | 43A4 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 166 | 17317 | 43A5 | 03/04 Read
[11 empty] | 167 | 17318 | 43A6 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 168 | 17319 | 43A7 | 03/04 Read
[11 empty] | 169 | 17320 | 43A8 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 170 | 17321 | 43A9 | 03/04 Read
[11 empty] | 171 | 17322 | 43AA | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 172 | 17323 | 43AB | 03/04 Read
[11 empty] | 173 | 17324 | 43AC | 03/04 Read | Phase A Circuit Deep Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 174 | 17325 | 43AD | 03/04 Read
[11 empty] | 175 | 17326 | 43AE | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 176 | 17327 | 43AF | 03/04 Read
[11 empty] | 177 | 17328 | 43B0 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 178 | 17329 | 43B1 | 03/04 Read
[11 empty] | 179 | 17330 | 43B2 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 180 | 17331 | 43B3 | 03/04 Read
[11 empty] | 181 | 17332 | 43B4 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 182 | 17333 | 43B5 | 03/04 Read
[11 empty] | 183 | 17334 | 43B6 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 184 | 17335 | 43B7 | 03/04 Read
[11 empty] | 185 | 17336 | 43B8 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 186 | 17337 | 43B9 | 03/04 Read
[11 empty] | 187 | Reserved
188
[11 empty] | 189 | 17340 | 43BC | 03/04 Read | Phase B Circuit Total Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 190 | 17341 | 43BD | 03/04 Read
[11 empty] | 191 | 17342 | 43BE | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 192 | 17343 | 43BF | 03/04 Read
[11 empty] | 193 | 17344 | 43C0 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 194 | 17345 | 43C1 | 03/04 Read
[11 empty] | 195 | 17346 | 43C2 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 196 | 17347 | 43C3 | 03/04 Read
[11 empty] | 197 | 17348 | 43C4 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 198 | 17349 | 43C5 | 03/04 Read
[11 empty] | 199 | 17350 | 43C6 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 200 | 17351 | 43C7 | 03/04 Read
[11 empty] | 201 | 17352 | 43C8 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 202 | 17353 | 43C9 | 03/04 Read
[11 empty] | 203 | 17354 | 43CA | 03/04 Read |  | 1st quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 204 | 17355 | 43CB | 03/04 Read
[11 empty] | 205 | 17356 | 43CC | 03/04 Read |  | 2nd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 206 | 17357 | 43CD | 03/04 Read
[11 empty] | 207 | 17358 | 43CE | 03/04 Read |  | 3rd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 208 | 17359 | 43CF | 03/04 Read
[11 empty] | 209 | 17360 | 43D0 | 03/04 Read |  | 4th quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 210 | 17361 | 43D1 | 03/04 Read
[11 empty] | 211 | 17362 | 43D2 | 03/04 Read | Phase B Circuit Sharp-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 212 | 17363 | 43D3 | 03/04 Read
[11 empty] | 213 | 17364 | 43D4 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 214 | 17365 | 43D5 | 03/04 Read
[11 empty] | 215 | 17366 | 43D6 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 216 | 17367 | 43D7 | 03/04 Read
[11 empty] | 217 | 17368 | 43D8 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 218 | 17369 | 43D9 | 03/04 Read
[11 empty] | 219 | 17370 | 43DA | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 220 | 17371 | 43DB | 03/04 Read
[11 empty] | 221 | 17372 | 43DC | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 222 | 17373 | 43DD | 03/04 Read
[11 empty] | 223 | 17374 | 43DE | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 224 | 17375 | 43DF | 03/04 Read
[11 empty] | 225 | 17376 | 43E0 | 03/04 Read | Phase B Circuit Peak-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 226 | 17377 | 43E1 | 03/04 Read
[11 empty] | 227 | 17378 | 43E2 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 228 | 17379 | 43E3 | 03/04 Read
[11 empty] | 229 | 17380 | 43E4 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 230 | 17381 | 43E5 | 03/04 Read
[11 empty] | 231 | 17382 | 43E6 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 232 | 17383 | 43E7 | 03/04 Read
[11 empty] | 233 | 17384 | 43E8 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 234 | 17385 | 43E9 | 03/04 Read
[11 empty] | 235 | 17386 | 43EA | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 236 | 17387 | 43EB | 03/04 Read
[11 empty] | 237 | 17388 | 43EC | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 238 | 17389 | 43ED | 03/04 Read
[11 empty] | 239 | 17390 | 43EE | 03/04 Read | Phase B Circuit Flat-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 240 | 17391 | 43EF | 03/04 Read
[11 empty] | 241 | 17392 | 43F0 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 242 | 17393 | 43F1 | 03/04 Read
[11 empty] | 243 | 17394 | 43F2 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 244 | 17395 | 43F3 | 03/04 Read
[11 empty] | 245 | 17396 | 43F4 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 246 | 17397 | 43F5 | 03/04 Read
[11 empty] | 247 | 17398 | 43F6 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 248 | 17399 | 43F7 | 03/04 Read
[11 empty] | 249 | 17400 | 43F8 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 250 | 17401 | 43F9 | 03/04 Read
[11 empty] | 251 | 17402 | 43FA | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 252 | 17403 | 43FB | 03/04 Read
[11 empty] | 253 | 17404 | 43FC | 03/04 Read | Phase B Circuit Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 254 | 17405 | 43FD | 03/04 Read
[11 empty] | 255 | 17406 | 43FE | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 256 | 17407 | 43FF | 03/04 Read
[11 empty] | 257 | 17408 | 4400 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 258 | 17409 | 4401 | 03/04 Read
[11 empty] | 259 | 17410 | 4402 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 260 | 17411 | 4403 | 03/04 Read
[11 empty] | 261 | 17412 | 4404 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 262 | 17413 | 4405 | 03/04 Read
[11 empty] | 263 | 17414 | 4406 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 264 | 17415 | 4407 | 03/04 Read
[11 empty] | 265 | 17416 | 4408 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 266 | 17417 | 4409 | 03/04 Read
[11 empty] | 267 | 17418 | 440A | 03/04 Read | Phase B Circuit Deep Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 268 | 17419 | 440B | 03/04 Read
[11 empty] | 269 | 17420 | 440C | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 270 | 17421 | 440D | 03/04 Read
[11 empty] | 271 | 17422 | 440E | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 272 | 17423 | 440F | 03/04 Read
[11 empty] | 273 | 17424 | 4410 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 274 | 17425 | 4411 | 03/04 Read
[11 empty] | 275 | 17426 | 4412 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 276 | 17427 | 4413 | 03/04 Read
[11 empty] | 277 | 17428 | 4414 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 278 | 17429 | 4415 | 03/04 Read
[11 empty] | 279 | 17430 | 4416 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 280 | 17431 | 4417 | 03/04 Read
[11 empty] | 281 | Reserved
282
[11 empty] | 283 | 17434 | 441A | 03/04 Read | Phase C Circuit Total Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 284 | 17435 | 441B | 03/04 Read
[11 empty] | 285 | 17436 | 441C | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 286 | 17437 | 441D | 03/04 Read
[11 empty] | 287 | 17438 | 441E | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 288 | 17439 | 441F | 03/04 Read
[11 empty] | 289 | 17440 | 4420 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 290 | 17441 | 4421 | 03/04 Read
[11 empty] | 291 | 17442 | 4422 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 292 | 17443 | 4423 | 03/04 Read
[11 empty] | 293 | 17444 | 4424 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 294 | 17445 | 4425 | 03/04 Read
[11 empty] | 295 | 17446 | 4426 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 296 | 17447 | 4427 | 03/04 Read
[11 empty] | 297 | 17448 | 4428 | 03/04 Read |  | 1st quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 298 | 17449 | 4429 | 03/04 Read
[11 empty] | 299 | 17450 | 442A | 03/04 Read |  | 2nd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 300 | 17451 | 442B | 03/04 Read
[11 empty] | 301 | 17452 | 442C | 03/04 Read |  | 3rd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 302 | 17453 | 442D | 03/04 Read
[11 empty] | 303 | 17454 | 442E | 03/04 Read |  | 4th quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 304 | 17455 | 442F | 03/04 Read
[11 empty] | 305 | 17456 | 4430 | 03/04 Read | Phase C Circuit Sharp-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 306 | 17457 | 4431 | 03/04 Read
[11 empty] | 307 | 17458 | 4432 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 308 | 17459 | 4433 | 03/04 Read
[11 empty] | 309 | 17460 | 4434 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 310 | 17461 | 4435 | 03/04 Read
[11 empty] | 311 | 17462 | 4436 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 312 | 17463 | 4437 | 03/04 Read
[11 empty] | 313 | 17464 | 4438 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 314 | 17465 | 4439 | 03/04 Read
[11 empty] | 315 | 17466 | 443A | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 316 | 17467 | 443B | 03/04 Read
[11 empty] | 317 | 17468 | 443C | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 318 | 17469 | 443D | 03/04 Read
[11 empty] | 319 | 17470 | 443E | 03/04 Read | Phase C Circuit Peak-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 320 | 17471 | 443F | 03/04 Read
[11 empty] | 321 | 17472 | 4440 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 322 | 17473 | 4441 | 03/04 Read
[11 empty] | 323 | 17474 | 4442 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 324 | 17475 | 4443 | 03/04 Read
[11 empty] | 325 | 17476 | 4444 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 326 | 17477 | 4445 | 03/04 Read
[11 empty] | 327 | 17478 | 4446 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 328 | 17479 | 4447 | 03/04 Read
[11 empty] | 329 | 17480 | 4448 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 330 | 17481 | 4449 | 03/04 Read
[11 empty] | 331 | 17482 | 444A | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 332 | 17483 | 444B | 03/04 Read
[11 empty] | 333 | 17484 | 444C | 03/04 Read | Phase C Circuit Flat-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 334 | 17485 | 444D | 03/04 Read
[11 empty] | 335 | 17486 | 444E | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 336 | 17487 | 444F | 03/04 Read
[11 empty] | 337 | 17488 | 4450 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 338 | 17489 | 4451 | 03/04 Read
[11 empty] | 339 | 17490 | 4452 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 340 | 17491 | 4453 | 03/04 Read
[11 empty] | 341 | 17492 | 4454 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 342 | 17493 | 4455 | 03/04 Read
[11 empty] | 343 | 17494 | 4456 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 344 | 17495 | 4457 | 03/04 Read
[11 empty] | 345 | 17496 | 4458 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 346 | 17497 | 4459 | 03/04 Read
[11 empty] | 347 | 17498 | 445A | 03/04 Read | Phase C Circuit Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 348 | 17499 | 445B | 03/04 Read
[11 empty] | 349 | 17500 | 445C | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 350 | 17501 | 445D | 03/04 Read
[11 empty] | 351 | 17502 | 445E | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 352 | 17503 | 445F | 03/04 Read
[11 empty] | 353 | 17504 | 4460 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 354 | 17505 | 4461 | 03/04 Read
[11 empty] | 355 | 17506 | 4462 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 356 | 17507 | 4463 | 03/04 Read
[11 empty] | 357 | 17508 | 4464 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 358 | 17509 | 4465 | 03/04 Read
[11 empty] | 359 | 17510 | 4466 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 360 | 17511 | 4467 | 03/04 Read
[11 empty] | 361 | 17512 | 4468 | 03/04 Read | Phase C Circuit Deep Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 362 | 17513 | 4469 | 03/04 Read
[11 empty] | 363 | 17514 | 446A | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 364 | 17515 | 446B | 03/04 Read
[11 empty] | 365 | 17516 | 446C | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 366 | 17517 | 446D | 03/04 Read
[11 empty] | 367 | 17518 | 446E | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 368 | 17519 | 446F | 03/04 Read
[11 empty] | 369 | 17520 | 4470 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 370 | 17521 | 4471 | 03/04 Read
[11 empty] | 371 | 17522 | 4472 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 372 | 17523 | 4473 | 03/04 Read
[11 empty] | 373 | 17524 | 4474 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 374 | 17525 | 4475 | 03/04 Read
[11 empty] | 375 | Reserved
376
The last Nth month multi-rate historical Energy Zone
[11 empty] | No, | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
[11 empty] | 1 | 17664 | 4500 |  |  | The Last Nth month | Unsigned 16-bit | 1 | 1~20 | - -
[11 empty] | 2 | 17665 | 4501 |  |  | Year Month | Unsigned 16-bit
[11 empty] | 3 | 17666 | 4502 |  |  | Day Hour
[11 empty] | 4 | 17667 | 4503 |  |  | Minute Second
[11 empty] | 5 | 17668 | 4504 | 03/04 Read | Total Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 6 | 17669 | 4505 | 03/04 Read
[11 empty] | 7 | 17670 | 4506 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 8 | 17671 | 4507 | 03/04 Read
[11 empty] | 9 | 17672 | 4508 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 10 | 17673 | 4509 | 03/04 Read
[11 empty] | 11 | 17674 | 450A | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 12 | 17675 | 450B | 03/04 Read
[11 empty] | 13 | 17676 | 450C | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 14 | 17677 | 450D | 03/04 Read
[11 empty] | 15 | 17678 | 450E | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 16 | 17679 | 450F | 03/04 Read
[11 empty] | 17 | 17680 | 4510 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 18 | 17681 | 4511 | 03/04 Read
[11 empty] | 19 | 17682 | 4512 | 03/04 Read |  | 1st quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 20 | 17683 | 4513 | 03/04 Read
[11 empty] | 21 | 17684 | 4514 | 03/04 Read |  | 2nd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 22 | 17685 | 4515 | 03/04 Read
[11 empty] | 23 | 17686 | 4516 | 03/04 Read |  | 3rd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 24 | 17687 | 4517 | 03/04 Read
[11 empty] | 25 | 17688 | 4518 | 03/04 Read |  | 4th quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 26 | 17689 | 4519 | 03/04 Read
[11 empty] | 27 | 17690 | 451A | 03/04 Read | Total Sharp-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 28 | 17691 | 451B | 03/04 Read
[11 empty] | 29 | 17692 | 451C | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 30 | 17693 | 451D | 03/04 Read
[11 empty] | 31 | 17694 | 451E | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 32 | 17695 | 451F | 03/04 Read
[11 empty] | 33 | 17696 | 4520 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 34 | 17697 | 4521 | 03/04 Read
[11 empty] | 35 | 17698 | 4522 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 36 | 17699 | 4523 | 03/04 Read
[11 empty] | 37 | 17700 | 4524 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 38 | 17701 | 4525 | 03/04 Read
[11 empty] | 39 | 17702 | 4526 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 40 | 17703 | 4527 | 03/04 Read
[11 empty] | 41 | 17704 | 4528 | 03/04 Read | Total Peak-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 42 | 17705 | 4529 | 03/04 Read
[11 empty] | 43 | 17706 | 452A | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 44 | 17707 | 452B | 03/04 Read
[11 empty] | 45 | 17708 | 452C | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 46 | 17709 | 452D | 03/04 Read
[11 empty] | 47 | 17710 | 452E | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 48 | 17711 | 452F | 03/04 Read
[11 empty] | 49 | 17712 | 4530 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 50 | 17713 | 4531 | 03/04 Read
[11 empty] | 51 | 17714 | 4532 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 52 | 17715 | 4533 | 03/04 Read
[11 empty] | 53 | 17716 | 4534 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 54 | 17717 | 4535 | 03/04 Read
[11 empty] | 55 | 17718 | 4536 | 03/04 Read | Total Flat-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 56 | 17719 | 4537 | 03/04 Read
[11 empty] | 57 | 17720 | 4538 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 58 | 17721 | 4539 | 03/04 Read
[11 empty] | 59 | 17722 | 453A | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 60 | 17723 | 453B | 03/04 Read
[11 empty] | 61 | 17724 | 453C | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 62 | 17725 | 453D | 03/04 Read
[11 empty] | 63 | 17726 | 453E | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 64 | 17727 | 453F | 03/04 Read
[11 empty] | 65 | 17728 | 4540 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 66 | 17729 | 4541 | 03/04 Read
[11 empty] | 67 | 17730 | 4542 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 68 | 17731 | 4543 | 03/04 Read
[11 empty] | 69 | 17732 | 4544 | 03/04 Read | Total Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 70 | 17733 | 4545 | 03/04 Read
[11 empty] | 71 | 17734 | 4546 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 72 | 17735 | 4547 | 03/04 Read
[11 empty] | 73 | 17736 | 4548 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 74 | 17737 | 4549 | 03/04 Read
[11 empty] | 75 | 17738 | 454A | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 76 | 17739 | 454B | 03/04 Read
[11 empty] | 77 | 17740 | 454C | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 78 | 17741 | 454D | 03/04 Read
[11 empty] | 79 | 17742 | 454E | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 80 | 17743 | 454F | 03/04 Read
[11 empty] | 81 | 17744 | 4550 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 82 | 17745 | 4551 | 03/04 Read
[11 empty] | 83 | 17746 | 4552 | 03/04 Read | Total Deep Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 84 | 17747 | 4553 | 03/04 Read
[11 empty] | 85 | 17748 | 4554 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 86 | 17749 | 4555 | 03/04 Read
[11 empty] | 87 | 17750 | 4556 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 88 | 17751 | 4557 | 03/04 Read
[11 empty] | 89 | 17752 | 4558 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 90 | 17753 | 4559 | 03/04 Read
[11 empty] | 91 | 17754 | 455A | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 92 | 17755 | 455B | 03/04 Read
[11 empty] | 93 | 17756 | 455C | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 94 | 17757 | 455D | 03/04 Read
[11 empty] | 95 | 17758 | 455E | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 96 | 17759 | 455F | 03/04 Read
[11 empty] | 97 | Reserved
98
[11 empty] | 99 | 17762 | 4562 | 03/04 Read | Phase A Circuit Total Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 100 | 17763 | 4563 | 03/04 Read
[11 empty] | 101 | 17764 | 4564 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 102 | 17765 | 4565 | 03/04 Read
[11 empty] | 103 | 17766 | 4566 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 104 | 17767 | 4567 | 03/04 Read
[11 empty] | 105 | 17768 | 4568 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 106 | 17769 | 4569 | 03/04 Read
[11 empty] | 107 | 17770 | 456A | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 108 | 17771 | 456B | 03/04 Read
[11 empty] | 109 | 17772 | 456C | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 110 | 17773 | 456D | 03/04 Read
[11 empty] | 111 | 17774 | 456E | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 112 | 17775 | 456F | 03/04 Read
[11 empty] | 113 | 17776 | 4570 | 03/04 Read |  | 1st quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 114 | 17777 | 4571 | 03/04 Read
[11 empty] | 115 | 17778 | 4572 | 03/04 Read |  | 2nd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 116 | 17779 | 4573 | 03/04 Read
[11 empty] | 117 | 17780 | 4574 | 03/04 Read |  | 3rd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 118 | 17781 | 4575 | 03/04 Read
[11 empty] | 119 | 17782 | 4576 | 03/04 Read |  | 4th quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 120 | 17783 | 4577 | 03/04 Read
[11 empty] | 121 | 17784 | 4578 | 03/04 Read | Phase A Circuit Sharp-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 122 | 17785 | 4579 | 03/04 Read
[11 empty] | 123 | 17786 | 457A | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 124 | 17787 | 457B | 03/04 Read
[11 empty] | 125 | 17788 | 457C | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 126 | 17789 | 457D | 03/04 Read
[11 empty] | 127 | 17790 | 457E | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 128 | 17791 | 457F | 03/04 Read
[11 empty] | 129 | 17792 | 4580 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 130 | 17793 | 4581 | 03/04 Read
[11 empty] | 131 | 17794 | 4582 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 132 | 17795 | 4583 | 03/04 Read
[11 empty] | 133 | 17796 | 4584 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 134 | 17797 | 4585 | 03/04 Read
[11 empty] | 135 | 17798 | 4586 | 03/04 Read | Phase A Circuit Peak-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 136 | 17799 | 4587 | 03/04 Read
[11 empty] | 137 | 17800 | 4588 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 138 | 17801 | 4589 | 03/04 Read
[11 empty] | 139 | 17802 | 458A | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 140 | 17803 | 458B | 03/04 Read
[11 empty] | 141 | 17804 | 458C | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 142 | 17805 | 458D | 03/04 Read
[11 empty] | 143 | 17806 | 458E | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 144 | 17807 | 458F | 03/04 Read
[11 empty] | 145 | 17808 | 4590 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 146 | 17809 | 4591 | 03/04 Read
[11 empty] | 147 | 17810 | 4592 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 148 | 17811 | 4593 | 03/04 Read
[11 empty] | 149 | 17812 | 4594 | 03/04 Read | Phase A Circuit Flat-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 150 | 17813 | 4595 | 03/04 Read
[11 empty] | 151 | 17814 | 4596 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 152 | 17815 | 4597 | 03/04 Read
[11 empty] | 153 | 17816 | 4598 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 154 | 17817 | 4599 | 03/04 Read
[11 empty] | 155 | 17818 | 459A | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 156 | 17819 | 459B | 03/04 Read
[11 empty] | 157 | 17820 | 459C | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 158 | 17821 | 459D | 03/04 Read
[11 empty] | 159 | 17822 | 459E | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 160 | 17823 | 459F | 03/04 Read
[11 empty] | 161 | 17824 | 45A0 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 162 | 17825 | 45A1 | 03/04 Read
[11 empty] | 163 | 17826 | 45A2 | 03/04 Read | Phase A Circuit Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 164 | 17827 | 45A3 | 03/04 Read
[11 empty] | 165 | 17828 | 45A4 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 166 | 17829 | 45A5 | 03/04 Read
[11 empty] | 167 | 17830 | 45A6 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 168 | 17831 | 45A7 | 03/04 Read
[11 empty] | 169 | 17832 | 45A8 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 170 | 17833 | 45A9 | 03/04 Read
[11 empty] | 171 | 17834 | 45AA | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 172 | 17835 | 45AB | 03/04 Read
[11 empty] | 173 | 17836 | 45AC | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 174 | 17837 | 45AD | 03/04 Read
[11 empty] | 175 | 17838 | 45AE | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 176 | 17839 | 45AF | 03/04 Read
[11 empty] | 177 | 17840 | 45B0 | 03/04 Read | Phase A Circuit Deep Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 178 | 17841 | 45B1 | 03/04 Read
[11 empty] | 179 | 17842 | 45B2 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 180 | 17843 | 45B3 | 03/04 Read
[11 empty] | 181 | 17844 | 45B4 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 182 | 17845 | 45B5 | 03/04 Read
[11 empty] | 183 | 17846 | 45B6 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 184 | 17847 | 45B7 | 03/04 Read
[11 empty] | 185 | 17848 | 45B8 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 186 | 17849 | 45B9 | 03/04 Read
[11 empty] | 187 | 17850 | 45BA | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 188 | 17851 | 45BB | 03/04 Read
[11 empty] | 189 | 17852 | 45BC | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 190 | 17853 | 45BD | 03/04 Read
[11 empty] | 191 | Reserved
192
[11 empty] | 193 | 17856 | 45C0 | 03/04 Read | Phase B Circuit Total Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 194 | 17857 | 45C1 | 03/04 Read
[11 empty] | 195 | 17858 | 45C2 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 196 | 17859 | 45C3 | 03/04 Read
[11 empty] | 197 | 17860 | 45C4 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 198 | 17861 | 45C5 | 03/04 Read
[11 empty] | 199 | 17862 | 45C6 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 200 | 17863 | 45C7 | 03/04 Read
[11 empty] | 201 | 17864 | 45C8 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 202 | 17865 | 45C9 | 03/04 Read
[11 empty] | 203 | 17866 | 45CA | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 204 | 17867 | 45CB | 03/04 Read
[11 empty] | 205 | 17868 | 45CC | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 206 | 17869 | 45CD | 03/04 Read
[11 empty] | 207 | 17870 | 45CE | 03/04 Read |  | 1st quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 208 | 17871 | 45CF | 03/04 Read
[11 empty] | 209 | 17872 | 45D0 | 03/04 Read |  | 2nd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 210 | 17873 | 45D1 | 03/04 Read
[11 empty] | 211 | 17874 | 45D2 | 03/04 Read |  | 3rd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 212 | 17875 | 45D3 | 03/04 Read
[11 empty] | 213 | 17876 | 45D4 | 03/04 Read |  | 4th quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 214 | 17877 | 45D5 | 03/04 Read
[11 empty] | 215 | 17878 | 45D6 | 03/04 Read | Phase B Circuit Sharp-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 216 | 17879 | 45D7 | 03/04 Read
[11 empty] | 217 | 17880 | 45D8 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 218 | 17881 | 45D9 | 03/04 Read
[11 empty] | 219 | 17882 | 45DA | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 220 | 17883 | 45DB | 03/04 Read
[11 empty] | 221 | 17884 | 45DC | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 222 | 17885 | 45DD | 03/04 Read
[11 empty] | 223 | 17886 | 45DE | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 224 | 17887 | 45DF | 03/04 Read
[11 empty] | 225 | 17888 | 45E0 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 226 | 17889 | 45E1 | 03/04 Read
[11 empty] | 227 | 17890 | 45E2 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 228 | 17891 | 45E3 | 03/04 Read
[11 empty] | 229 | 17892 | 45E4 | 03/04 Read | Phase B Circuit Peak-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 230 | 17893 | 45E5 | 03/04 Read
[11 empty] | 231 | 17894 | 45E6 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 232 | 17895 | 45E7 | 03/04 Read
[11 empty] | 233 | 17896 | 45E8 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 234 | 17897 | 45E9 | 03/04 Read
[11 empty] | 235 | 17898 | 45EA | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 236 | 17899 | 45EB | 03/04 Read
[11 empty] | 237 | 17900 | 45EC | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 238 | 17901 | 45ED | 03/04 Read
[11 empty] | 239 | 17902 | 45EE | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 240 | 17903 | 45EF | 03/04 Read
[11 empty] | 241 | 17904 | 45F0 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 242 | 17905 | 45F1 | 03/04 Read
[11 empty] | 243 | 17906 | 45F2 | 03/04 Read | Phase B Circuit Flat-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 244 | 17907 | 45F3 | 03/04 Read
[11 empty] | 245 | 17908 | 45F4 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 246 | 17909 | 45F5 | 03/04 Read
[11 empty] | 247 | 17910 | 45F6 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 248 | 17911 | 45F7 | 03/04 Read
[11 empty] | 249 | 17912 | 45F8 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 250 | 17913 | 45F9 | 03/04 Read
[11 empty] | 251 | 17914 | 45FA | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 252 | 17915 | 45FB | 03/04 Read
[11 empty] | 253 | 17916 | 45FC | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 254 | 17917 | 45FD | 03/04 Read
[11 empty] | 255 | 17918 | 45FE | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 256 | 17919 | 45FF | 03/04 Read
[11 empty] | 257 | 17920 | 4600 | 03/04 Read | Phase B Circuit Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 258 | 17921 | 4601 | 03/04 Read
[11 empty] | 259 | 17922 | 4602 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 260 | 17923 | 4603 | 03/04 Read
[11 empty] | 261 | 17924 | 4604 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 262 | 17925 | 4605 | 03/04 Read
[11 empty] | 263 | 17926 | 4606 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 264 | 17927 | 4607 | 03/04 Read
[11 empty] | 265 | 17928 | 4608 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 266 | 17929 | 4609 | 03/04 Read
[11 empty] | 267 | 17930 | 460A | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 268 | 17931 | 460B | 03/04 Read
[11 empty] | 269 | 17932 | 460C | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 270 | 17933 | 460D | 03/04 Read
[11 empty] | 271 | 17934 | 460E | 03/04 Read | Phase B Circuit Deep Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 272 | 17935 | 460F | 03/04 Read
[11 empty] | 273 | 17936 | 4610 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 274 | 17937 | 4611 | 03/04 Read
[11 empty] | 275 | 17938 | 4612 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 276 | 17939 | 4613 | 03/04 Read
[11 empty] | 277 | 17940 | 4614 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 278 | 17941 | 4615 | 03/04 Read
[11 empty] | 279 | 17942 | 4616 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 280 | 17943 | 4617 | 03/04 Read
[11 empty] | 281 | 17944 | 4618 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 282 | 17945 | 4619 | 03/04 Read
[11 empty] | 283 | 17946 | 461A | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 284 | 17947 | 461B | 03/04 Read
[11 empty] | 285 | Reserved
286
[11 empty] | 287 | 17950 | 461E | 03/04 Read | Phase C Circuit Total Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 288 | 17951 | 461F | 03/04 Read
[11 empty] | 289 | 17952 | 4620 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 290 | 17953 | 4621 | 03/04 Read
[11 empty] | 291 | 17954 | 4622 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 292 | 17955 | 4623 | 03/04 Read
[11 empty] | 293 | 17956 | 4624 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 294 | 17957 | 4625 | 03/04 Read
[11 empty] | 295 | 17958 | 4626 | 03/04 Read |  |  | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 296 | 17959 | 4627 | 03/04 Read
[11 empty] | 297 | 17960 | 4628 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 298 | 17961 | 4629 | 03/04 Read
[11 empty] | 299 | 17962 | 462A | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 300 | 17963 | 462B | 03/04 Read
[11 empty] | 301 | 17964 | 462C | 03/04 Read |  | 1st quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 302 | 17965 | 462D | 03/04 Read
[11 empty] | 303 | 17966 | 462E | 03/04 Read |  | 2nd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 304 | 17967 | 462F | 03/04 Read
[11 empty] | 305 | 17968 | 4630 | 03/04 Read |  | 3rd quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 306 | 17969 | 4631 | 03/04 Read
[11 empty] | 307 | 17970 | 4632 | 03/04 Read |  | 4th quadrant reactive energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 308 | 17971 | 4633 | 03/04 Read
[11 empty] | 309 | 17972 | 4634 | 03/04 Read | Phase C Circuit Sharp-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 310 | 17973 | 4635 | 03/04 Read
[11 empty] | 311 | 17974 | 4636 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 312 | 17975 | 4637 | 03/04 Read
[11 empty] | 313 | 17976 | 4638 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 314 | 17977 | 4639 | 03/04 Read
[11 empty] | 315 | 17978 | 463A | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 316 | 17979 | 463B | 03/04 Read
[11 empty] | 317 | 17980 | 463C | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 318 | 17981 | 463D | 03/04 Read
[11 empty] | 319 | 17982 | 463E | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 320 | 17983 | 463F | 03/04 Read
[11 empty] | 321 | 17984 | 4640 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 322 | 17985 | 4641 | 03/04 Read
[11 empty] | 323 | 17986 | 4642 | 03/04 Read | Phase C Circuit Peak-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 324 | 17987 | 4643 | 03/04 Read
[11 empty] | 325 | 17988 | 4644 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 326 | 17989 | 4645 | 03/04 Read
[11 empty] | 327 | 17990 | 4646 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 328 | 17991 | 4647 | 03/04 Read
[11 empty] | 329 | 17992 | 4648 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 330 | 17993 | 4649 | 03/04 Read
[11 empty] | 331 | 17994 | 464A | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 332 | 17995 | 464B | 03/04 Read
[11 empty] | 333 | 17996 | 464C | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 334 | 17997 | 464D | 03/04 Read
[11 empty] | 335 | 17998 | 464E | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 336 | 17999 | 464F | 03/04 Read
[11 empty] | 337 | 18000 | 4650 | 03/04 Read | Phase C Circuit Flat-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 338 | 18001 | 4651 | 03/04 Read
[11 empty] | 339 | 18002 | 4652 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 340 | 18003 | 4653 | 03/04 Read
[11 empty] | 341 | 18004 | 4654 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 342 | 18005 | 4655 | 03/04 Read
[11 empty] | 343 | 18006 | 4656 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 344 | 18007 | 4657 | 03/04 Read
[11 empty] | 345 | 18008 | 4658 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 346 | 18009 | 4659 | 03/04 Read
[11 empty] | 347 | 18010 | 465A | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 348 | 18011 | 465B | 03/04 Read
[11 empty] | 349 | 18012 | 465C | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 350 | 18013 | 465D | 03/04 Read
[11 empty] | 351 | 18014 | 465E | 03/04 Read | Phase C Circuit Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 352 | 18015 | 465F | 03/04 Read
[11 empty] | 353 | 18016 | 4660 | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 354 | 18017 | 4661 | 03/04 Read
[11 empty] | 355 | 18018 | 4662 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 356 | 18019 | 4663 | 03/04 Read
[11 empty] | 357 | 18020 | 4664 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 358 | 18021 | 4665 | 03/04 Read
[11 empty] | 359 | 18022 | 4666 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 360 | 18023 | 4667 | 03/04 Read
[11 empty] | 361 | 18024 | 4668 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 362 | 18025 | 4669 | 03/04 Read
[11 empty] | 363 | 18026 | 466A | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 364 | 18027 | 466B | 03/04 Read
[11 empty] | 365 | 18028 | 466C | 03/04 Read | Phase C Circuit Deep Valley-period Energy | Total Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 366 | 18029 | 466D | 03/04 Read
[11 empty] | 367 | 18030 | 466E | 03/04 Read |  | Import Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 368 | 18031 | 466F | 03/04 Read
[11 empty] | 369 | 18032 | 4670 | 03/04 Read |  | Export Active Energy | Unsigned 32-bit | 0 | 0～999999999 | kWh | magnifying 100 times
[11 empty] | 370 | 18033 | 4671 | 03/04 Read
[11 empty] | 371 | 18034 | 4672 | 03/04 Read |  | Total Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 372 | 18035 | 4673 | 03/04 Read
[11 empty] | 373 | 18036 | 4674 | 03/04 Read |  | Import Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 374 | 18037 | 4675 | 03/04 Read
[11 empty] | 375 | 18038 | 4676 | 03/04 Read |  | Export Reactive Energy | Unsigned 32-bit | 0 | 0～999999999 | kvarh | magnifying 100 times
[11 empty] | 376 | 18039 | 4677 | 03/04 Read
[11 empty] | 377 | 18040 | 4678 | 03/04 Read |  | Apparent Energy | Unsigned 32-bit | 0 | 0～999999999 | kVA | magnifying 100 times
[11 empty] | 378 | 18041 | 4679 | 03/04 Read

## THD
THD（Function Code 04, read） | Harmonic Distortion Parameter
| No. | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
4352 | 1 | 4352 | 1100 | 03/04 read | Total Harmonic Distortion Rate (THD) | line/phase voltage THD of phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4353 | 2 | 4353 | 1101 | 03/04 read |  | line/phase voltage THD of phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4354 | 3 | 4354 | 1102 | 03/04 read |  | line/phase voltage THD of phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4355 | 4 | 4355 | 1103 | 03/04 read |  | line/phase voltage mean value THD | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4356 | 5 | 4356 | 1104 | 03/04 read |  | current THD of phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4357 | 6 | 4357 | 1105 | 03/04 read |  | current THD of phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4358 | 7 | 4358 | 1106 | 03/04 read |  | current THD of phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4359 | 8 | 4359 | 1107 | 03/04 read |  | current mean value THD | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4360 | 9 | 4360 | 1108 | 03/04 read | (Odd) Phase A Voltage Harmonic Content | 3rd line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4361 | 10 | 4361 | 1109 | 03/04 read |  | 5th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4362 | 11 | 4362 | 110A | 03/04 read |  | 7th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4363 | 12 | 4363 | 110B | 03/04 read |  | 9th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4364 | 13 | 4364 | 110C | 03/04 read |  | 11th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4365 | 14 | 4365 | 110D | 03/04 read |  | 13th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4366 | 15 | 4366 | 110E | 03/04 read |  | 15th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4367 | 16 | 4367 | 110F | 03/04 read |  | 17th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4368 | 17 | 4368 | 1110 | 03/04 read |  | 19th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4369 | 18 | 4369 | 1111 | 03/04 read |  | 21st line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4370 | 19 | 4370 | 1112 | 03/04 read |  | 23rd line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4371 | 20 | 4371 | 1113 | 03/04 read |  | 25th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4372 | 21 | 4372 | 1114 | 03/04 read |  | 27th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4373 | 22 | 4373 | 1115 | 03/04 read |  | 29th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4374 | 23 | 4374 | 1116 | 03/04 read |  | 31st line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4375 | 24 | 4375 | 1117 | 03/04 read | (Even) Phase A Voltage Harmonic Content | 2nd line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4376 | 25 | 4376 | 1118 | 03/04 read |  | 4th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4377 | 26 | 4377 | 1119 | 03/04 read |  | 6th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4378 | 27 | 4378 | 111A | 03/04 read |  | 8th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4379 | 28 | 4379 | 111B | 03/04 read |  | 10th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4380 | 29 | 4380 | 111C | 03/04 read |  | 12th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4381 | 30 | 4381 | 111D | 03/04 read |  | 14th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4382 | 31 | 4382 | 111E | 03/04 read |  | 16th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4383 | 32 | 4383 | 111F | 03/04 read |  | 18th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4384 | 33 | 4384 | 1120 | 03/04 read |  | 20th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4385 | 34 | 4385 | 1121 | 03/04 read |  | 22nd line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4386 | 35 | 4386 | 1122 | 03/04 read |  | 24th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4387 | 36 | 4387 | 1123 | 03/04 read |  | 26th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4388 | 37 | 4388 | 1124 | 03/04 read |  | 28th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4389 | 38 | 4389 | 1125 | 03/04 read |  | 30th line/phase voltage harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4390 | 39 | 4390 | 1126 | 03/04 read | Phase A Voltage Harmonic Analysis | odd line/phase voltage harmonic distortion rate of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4391 | 40 | 4391 | 1127 | 03/04 read |  | even line/phase voltage harmonic distortion rate of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4392 | 41 | 4392 | 1128 | 03/04 read |  | reserved | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4393 | 42 | 4393 | 1129 | 03/04 read |  | reserved | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4394 | 43 | 4394 | 112A | 03/04 read | Phase B Voltage(Odd) Harmonic Content | 3rd line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4395 | 44 | 4395 | 112B | 03/04 read |  | 5th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4396 | 45 | 4396 | 112C | 03/04 read |  | 7th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4397 | 46 | 4397 | 112D | 03/04 read |  | 9th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4398 | 47 | 4398 | 112E | 03/04 read |  | 11th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4399 | 48 | 4399 | 112F | 03/04 read |  | 13th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4400 | 49 | 4400 | 1130 | 03/04 read |  | 15th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4401 | 50 | 4401 | 1131 | 03/04 read |  | 17th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4402 | 51 | 4402 | 1132 | 03/04 read |  | 19th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4403 | 52 | 4403 | 1133 | 03/04 read |  | 21st line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4404 | 53 | 4404 | 1134 | 03/04 read |  | 23rd line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4405 | 54 | 4405 | 1135 | 03/04 read |  | 25th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4406 | 55 | 4406 | 1136 | 03/04 read |  | 27th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4407 | 56 | 4407 | 1137 | 03/04 read |  | 29th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4408 | 57 | 4408 | 1138 | 03/04 read |  | 31st line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4409 | 58 | 4409 | 1139 | 03/04 read | (Even) Phase B Voltage Harmonic Content | 2nd line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4410 | 59 | 4410 | 113A | 03/04 read |  | 4th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4411 | 60 | 4411 | 113B | 03/04 read |  | 6th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4412 | 61 | 4412 | 113C | 03/04 read |  | 8th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4413 | 62 | 4413 | 113D | 03/04 read |  | 10th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4414 | 63 | 4414 | 113E | 03/04 read |  | 12th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4415 | 64 | 4415 | 113F | 03/04 read |  | 14th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4416 | 65 | 4416 | 1140 | 03/04 read |  | 16th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4417 | 66 | 4417 | 1141 | 03/04 read |  | 18th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4418 | 67 | 4418 | 1142 | 03/04 read |  | 20th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4419 | 68 | 4419 | 1143 | 03/04 read |  | 22nd line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4420 | 69 | 4420 | 1144 | 03/04 read |  | 24th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4421 | 70 | 4421 | 1145 | 03/04 read |  | 26th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4422 | 71 | 4422 | 1146 | 03/04 read |  | 28th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4423 | 72 | 4423 | 1147 | 03/04 read |  | 30th line/phase voltage harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4424 | 73 | 4424 | 1148 | 03/04 read | Phase B Voltage Harmonic Analysis | odd line/phase voltage harmonic distortion rate of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4425 | 74 | 4425 | 1149 | 03/04 read |  | even line/phase voltage harmonic distortion rate of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4426 | 75 | 4426 | 114A | 03/04 read |  | reserved | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4427 | 76 | 4427 | 114B | 03/04 read |  | reserved | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4428 | 77 | 4428 | 114C | 03/04 read | (Odd) Phase C Voltage Harmonic Content | 3rd line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4429 | 78 | 4429 | 114D | 03/04 read |  | 5th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4430 | 79 | 4430 | 114E | 03/04 read |  | 7th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4431 | 80 | 4431 | 114F | 03/04 read |  | 9th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4432 | 81 | 4432 | 1150 | 03/04 read |  | 11th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4433 | 82 | 4433 | 1151 | 03/04 read |  | 13th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4434 | 83 | 4434 | 1152 | 03/04 read |  | 15th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4435 | 84 | 4435 | 1153 | 03/04 read |  | 17th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4436 | 85 | 4436 | 1154 | 03/04 read |  | 19th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4437 | 86 | 4437 | 1155 | 03/04 read |  | 21st line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4438 | 87 | 4438 | 1156 | 03/04 read |  | 23rd line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4439 | 88 | 4439 | 1157 | 03/04 read |  | 25th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4440 | 89 | 4440 | 1158 | 03/04 read |  | 27th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4441 | 90 | 4441 | 1159 | 03/04 read |  | 29th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4442 | 91 | 4442 | 115A | 03/04 read |  | 31st line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4443 | 92 | 4443 | 115B | 03/04 read | (Even) Phase C Voltage Harmonic Content | 2nd line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4444 | 93 | 4444 | 115C | 03/04 read |  | 4th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4445 | 94 | 4445 | 115D | 03/04 read |  | 6th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4446 | 95 | 4446 | 115E | 03/04 read |  | 8th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4447 | 96 | 4447 | 115F | 03/04 read |  | 10th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4448 | 97 | 4448 | 1160 | 03/04 read |  | 12th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4449 | 98 | 4449 | 1161 | 03/04 read |  | 14th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4450 | 99 | 4450 | 1162 | 03/04 read |  | 16th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4451 | 100 | 4451 | 1163 | 03/04 read |  | 18th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4452 | 101 | 4452 | 1164 | 03/04 read |  | 20th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4453 | 102 | 4453 | 1165 | 03/04 read |  | 22nd line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4454 | 103 | 4454 | 1166 | 03/04 read |  | 24th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4455 | 104 | 4455 | 1167 | 03/04 read |  | 26th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4456 | 105 | 4456 | 1168 | 03/04 read |  | 28th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4457 | 106 | 4457 | 1169 | 03/04 read |  | 30th line/phase voltage harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4458 | 107 | 4458 | 116A | 03/04 read | Phase C Voltage Harmonic Analysis | odd line/phase voltage harmonic distortion rate of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4459 | 108 | 4459 | 116B | 03/04 read |  | even line/phase voltage harmonic distortion rate of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4460 | 109 | 4460 | 116C | 03/04 read |  | reserved | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4461 | 110 | 4461 | 116D | 03/04 read |  | reserved | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4462 | 111 | 4462 | 116E | 03/04 read | (Odd) Phase A Current Harmonic Content | 3rd current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4463 | 112 | 4463 | 116F | 03/04 read |  | 5th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4464 | 113 | 4464 | 1170 | 03/04 read |  | 7th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4465 | 114 | 4465 | 1171 | 03/04 read |  | 9th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4466 | 115 | 4466 | 1172 | 03/04 read |  | 11th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4467 | 116 | 4467 | 1173 | 03/04 read |  | 13th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4468 | 117 | 4468 | 1174 | 03/04 read |  | 15th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4469 | 118 | 4469 | 1175 | 03/04 read |  | 17th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4470 | 119 | 4470 | 1176 | 03/04 read |  | 19th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4471 | 120 | 4471 | 1177 | 03/04 read |  | 21st current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4472 | 121 | 4472 | 1178 | 03/04 read |  | 23rd current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4473 | 122 | 4473 | 1179 | 03/04 read |  | 25th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4474 | 123 | 4474 | 117A | 03/04 read |  | 27th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4475 | 124 | 4475 | 117B | 03/04 read |  | 29th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4476 | 125 | 4476 | 117C | 03/04 read |  | 31st current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4477 | 126 | 4477 | 117D | 03/04 read | (Even) Phase A Current Harmonic Content | 2nd current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4478 | 127 | 4478 | 117E | 03/04 read |  | 4th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4479 | 128 | 4479 | 117F | 03/04 read |  | 6th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4480 | 129 | 4480 | 1180 | 03/04 read |  | 8th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4481 | 130 | 4481 | 1181 | 03/04 read |  | 10th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4482 | 131 | 4482 | 1182 | 03/04 read |  | 12th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4483 | 132 | 4483 | 1183 | 03/04 read |  | 14th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4484 | 133 | 4484 | 1184 | 03/04 read |  | 16th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4485 | 134 | 4485 | 1185 | 03/04 read |  | 18th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4486 | 135 | 4486 | 1186 | 03/04 read |  | 20th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4487 | 136 | 4487 | 1187 | 03/04 read |  | 22nd current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4488 | 137 | 4488 | 1188 | 03/04 read |  | 24th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4489 | 138 | 4489 | 1189 | 03/04 read |  | 26th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4490 | 139 | 4490 | 118A | 03/04 read |  | 28th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4491 | 140 | 4491 | 118B | 03/04 read |  | 30th current harmonic content of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4492 | 141 | 4492 | 118C | 03/04 read | Phase A Current Harmonic Analysis | odd current harmonic distortion rate of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4493 | 142 | 4493 | 118D | 03/04 read |  | even current harmonic distortion rate of Phase A | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4494 | 143 | 4494 | 118E | 03/04 read |  | reserved | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4495 | 144 | 4495 | 118F | 03/04 read |  | reserved | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4496 | 145 | 4496 | 1190 | 03/04 read | (Odd) Phase B Current Harmonic Content | 3rd current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4497 | 146 | 4497 | 1191 | 03/04 read |  | 5th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4498 | 147 | 4498 | 1192 | 03/04 read |  | 7th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4499 | 148 | 4499 | 1193 | 03/04 read |  | 9th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4500 | 149 | 4500 | 1194 | 03/04 read |  | 11th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4501 | 150 | 4501 | 1195 | 03/04 read |  | 13th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4502 | 151 | 4502 | 1196 | 03/04 read |  | 15th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4503 | 152 | 4503 | 1197 | 03/04 read |  | 17th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4504 | 153 | 4504 | 1198 | 03/04 read |  | 19th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4505 | 154 | 4505 | 1199 | 03/04 read |  | 21st current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4506 | 155 | 4506 | 119A | 03/04 read |  | 23rd current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4507 | 156 | 4507 | 119B | 03/04 read |  | 25th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4508 | 157 | 4508 | 119C | 03/04 read |  | 27th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4509 | 158 | 4509 | 119D | 03/04 read |  | 29th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4510 | 159 | 4510 | 119E | 03/04 read |  | 31st current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4511 | 160 | 4511 | 119F | 03/04 read | (Even) Phase B Current Harmonic Content | 2nd current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4512 | 161 | 4512 | 11A0 | 03/04 read |  | 4th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4513 | 162 | 4513 | 11A1 | 03/04 read |  | 6th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4514 | 163 | 4514 | 11A2 | 03/04 read |  | 8th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4515 | 164 | 4515 | 11A3 | 03/04 read |  | 10th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4516 | 165 | 4516 | 11A4 | 03/04 read |  | 12th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4517 | 166 | 4517 | 11A5 | 03/04 read |  | 14th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4518 | 167 | 4518 | 11A6 | 03/04 read |  | 16th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4519 | 168 | 4519 | 11A7 | 03/04 read |  | 18th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4520 | 169 | 4520 | 11A8 | 03/04 read |  | 20th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4521 | 170 | 4521 | 11A9 | 03/04 read |  | 22nd current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4522 | 171 | 4522 | 11AA | 03/04 read |  | 24th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4523 | 172 | 4523 | 11AB | 03/04 read |  | 26th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4524 | 173 | 4524 | 11AC | 03/04 read |  | 28th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4525 | 174 | 4525 | 11AD | 03/04 read |  | 30th current harmonic content of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4526 | 175 | 4526 | 11AE | 03/04 read | Phase B Current Harmonic Analysis | odd current harmonic distortion rate of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4527 | 176 | 4527 | 11AF | 03/04 read |  | even current harmonic distortion rate of Phase B | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4528 | 177 | 4528 | 11B0 | 03/04 read |  | reserved | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4529 | 178 | 4529 | 11B1 | 03/04 read |  | reserved | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4530 | 179 | 4530 | 11B2 | 03/04 read | (Odd) Phase C Current Harmonic Content | 3rd current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4531 | 180 | 4531 | 11B3 | 03/04 read |  | 5th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4532 | 181 | 4532 | 11B4 | 03/04 read |  | 7th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4533 | 182 | 4533 | 11B5 | 03/04 read |  | 9th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4534 | 183 | 4534 | 11B6 | 03/04 read |  | 11th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4535 | 184 | 4535 | 11B7 | 03/04 read |  | 13th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4536 | 185 | 4536 | 11B8 | 03/04 read |  | 15th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4537 | 186 | 4537 | 11B9 | 03/04 read |  | 17th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4538 | 187 | 4538 | 11BA | 03/04 read |  | 19th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4539 | 188 | 4539 | 11BB | 03/04 read |  | 21st current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4540 | 189 | 4540 | 11BC | 03/04 read |  | 23rd current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4541 | 190 | 4541 | 11BD | 03/04 read |  | 25th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4542 | 191 | 4542 | 11BE | 03/04 read |  | 27th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4543 | 192 | 4543 | 11BF | 03/04 read |  | 29th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4544 | 193 | 4544 | 11C0 | 03/04 read |  | 31st current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4545 | 194 | 4545 | 11C1 | 03/04 read | (Even) Phase C Current Harmonic Content | 2nd current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4546 | 195 | 4546 | 11C2 | 03/04 read |  | 4th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4547 | 196 | 4547 | 11C3 | 03/04 read |  | 6th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4548 | 197 | 4548 | 11C4 | 03/04 read |  | 8th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4549 | 198 | 4549 | 11C5 | 03/04 read |  | 10th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4550 | 199 | 4550 | 11C6 | 03/04 read |  | 12th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4551 | 200 | 4551 | 11C7 | 03/04 read |  | 14th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4552 | 201 | 4552 | 11C8 | 03/04 read |  | 16th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4553 | 202 | 4553 | 11C9 | 03/04 read |  | 18th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4554 | 203 | 4554 | 11CA | 03/04 read |  | 20th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4555 | 204 | 4555 | 11CB | 03/04 read |  | 22nd current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4556 | 205 | 4556 | 11CC | 03/04 read |  | 24th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4557 | 206 | 4557 | 11CD | 03/04 read |  | 26th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4558 | 207 | 4558 | 11CE | 03/04 read |  | 28th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4559 | 208 | 4559 | 11CF | 03/04 read |  | 30th current harmonic content of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
4560 | 209 | 4560 | 11D0 | 03/04 read | Phase C Current Harmonic Analysis | odd current harmonic distortion rate of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
| 210 | 4561 | 11D1 | 03/04 read |  | even current harmonic distortion rate of Phase C | Unsigned 16-bit | 0 | 0～10000 | % | Rx/1000×100%
| 211 | 4562 | 11D2 | 03/04 read |  | reserved | Unsigned 16-bit | 0 |  | % | Rx/1000×100%
| 212 | 4563 | 11D3 | 03/04 read |  | reserved | Unsigned 16-bit | 0 |  | % | Rx/1000×100%
Remark： 1. The registers, named as "Reserved", in the harmonic parameter zone, have no function in this meter. And the data read from these registers can not be used for any reference, and theses registers are only reserved for future extended functions. 2. All the data of registers from 0x1100 to 0x11D0 are magnified 100 times.

## Multi Tarrif
[11 empty] | Multi rate Time Period Table 1 | [10 empty] | Multi rate Month Time Zone
Multi Tarrif（Function Code 04 Read） |  |  |  |  | Multi Tarrif Password Setting（Function Code 10H Write） | [5 empty] | No, | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark | No, | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter | Data Type | Default Value | Value Range | Unit | Remark
Category | Address (Decimal) | Address (Hexadecimal) | Parameter | Range | Category | Address (Decimal) | Address (Hexadecimal) | Parameter | Range
[11 empty] | 1 | 8448 | 2100 | 03 Read 06/10 Write | Multi Tarrif Period Setting | Rate of The 1st Period | Unsigned 16-bit | 2 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 1 | 9984 | 2700 | 03 Read 06/10 Write | Rate of The 1st Month Period | Unsigned 16-bit | 1 | refer to Multi rate Time Period Table 1/2/3/4 | ——
Present-month Energy (Total Energy) | 16640 | 4100 | Total Active Energy | 0~9999 9999.9 | Password | 52996 | CF04 | Period Password Setting | 8887H |  | 2 | 8449 | 2101 | 03 Read 06/10 Write |  | Start Time of The 1st Period: Hour, Minute | Unsigned 16-bit | 9:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 2 | 9985 | 2701 | 03 Read 06/10 Write | Start Time of The 1st Month Period: month, day | Unsigned 16-bit | 2024-02-01 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16641 | 4101 |  |  |  | 52997 | CF05 |  | 2666H |  | 3 | 8450 | 2102 | 03 Read 06/10 Write |  | End Time of The 1st Period: Hour, Minute | Unsigned 16-bit | 11:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 3 | 9986 | 2702 | 03 Read 06/10 Write | End Time of The 1st Month Period: month, day | Unsigned 16-bit | 2024-05-31 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16642 | 4102 | Import Active Energy | 0~9999 9999.9 | [6 empty] | 4 | 8451 | 2103 | 03 Read 06/10 Write |  | Rate of The 2st Period | Unsigned 16-bit | 2 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 4 | 9987 | 2703 | 03 Read 06/10 Write | Rate of The 2nd Month Period | Unsigned 16-bit | 2 | refer to Multi rate Time Period Table 1/2/3/4 | ——
| 16643 | 4103 |  |  | Multi Tarrif Period Setting（Function Code 03H、06H，10H） | [5 empty] | 5 | 8452 | 2104 | 03 Read 06/10 Write |  | Start Time of The 2st Period: Hour, Minute | Unsigned 16-bit | 15:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 5 | 9988 | 2704 | 03 Read 06/10 Write | Start Time of The 2nd Month Period: month, day | Unsigned 16-bit | 2024-06-01 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16644 | 4104 | Export Active Energy | 0~9999 9999.9 | Category | Address (Decimal) | Address (Hexadecimal) | Parameter | Default | Range | 6 | 8453 | 2105 | 03 Read 06/10 Write |  | End Time of The 2st Period: Hour, Minute | Unsigned 16-bit | 22:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 6 | 9989 | 2705 | 03 Read 06/10 Write | End Time of The 2nd Month Period: month, day | Unsigned 16-bit | 2024-08-31 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16645 | 4105 | [8 empty] | 7 | 8454 | 2106 | 03 Read 06/10 Write |  | Rate of The 3st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 7 | 9990 | 2706 | 03 Read 06/10 Write | Rate of The 3th Month Period | Unsigned 16-bit | 1 | refer to Multi rate Time Period Table 1/2/3/4 | ——
| 16646 | 4106 | Total Reactive Energy | 0~9999 9999.9 |  | 8448 | 2100 | Tarrif of The 1st Period | 3(Flat） | 1：sharp，2：Peak，3：Flat，4：Valley | 8 | 8455 | 2107 | 03 Read 06/10 Write |  | Start Time of The 3st Period: Hour, Minute | Unsigned 16-bit | 07:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 8 | 9991 | 2707 | 03 Read 06/10 Write | Start Time of The 3th Month Period: month, day | Unsigned 16-bit | 2024-09-01 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16647 | 4107 |  |  |  | 8449 | 2101 | Start Time of The 1st Period: Hour, Minute | 7:00 | High bit Hour:0~23 Low bit Minute:0~59 | 9 | 8456 | 2108 | 03 Read 06/10 Write |  | End Time of The 3st Period: Hour, Minute | Unsigned 16-bit | 09:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 9 | 9992 | 2708 | 03 Read 06/10 Write | End Time of The 3th Month Period: month, day | Unsigned 16-bit | 2024-11-30 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16648 | 4108 | Import Reactive Energy | 0~9999 9999.9 |  | 8450 | 2102 | End Time of The 1st Period: Hour, Minute | 8:30 | High bit Hour:0~23 Low bit Minute:0~59 | 10 | 8457 | 2109 | 03 Read 06/10 Write |  | Rate of The 4st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 10 | 9993 | 2709 | 03 Read 06/10 Write | Rate of The 4th Month Period | Unsigned 16-bit | 3 | refer to Multi rate Time Period Table 1/2/3/4 | ——
| 16649 | 4109 |  |  |  | 8451 | 2103 | Tarrif of The 2st Period | 2 (Peak) | 1：sharp，2：Peak，3：Flat，4：Valley | 11 | 8458 | 210A | 03 Read 06/10 Write |  | Start Time of The 4st Period: Hour, Minute | Unsigned 16-bit | 11:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 11 | 9994 | 270A | 03 Read 06/10 Write | Start Time of The 4th Month Period: month, day | Unsigned 16-bit | 2024-12-01 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16650 | 410A | Export Reactive Energy | 0~9999 9999.9 |  | 8452 | 2104 | Start Time of The 2st Period: Hour, Minute | 8:30 | High bit Hour:0~23 Low bit Minute:0~59 | 12 | 8459 | 210B | 03 Read 06/10 Write |  | End Time of The 4st Period: Hour, Minute | Unsigned 16-bit | 12:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 12 | 9995 | 270B | 03 Read 06/10 Write | End Time of The 4th Month Period: month, day | Unsigned 16-bit | 2024-01-31 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16651 | 410B |  |  |  | 8453 | 2105 | End Time of The 2st Period: Hour, Minute | 10:30 | High bit Hour:0~23 Low bit Minute:0~59 | 13 | 8460 | 210C | 03 Read 06/10 Write |  | Rate of The 5st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 13 | 9996 | 270C | 03 Read 06/10 Write | Rate of The 5th Month Period | Unsigned 16-bit | 0 | refer to Multi rate Time Period Table 1/2/3/4 | ——
Present-month Energy (Sharp-period Energy) | 16652 | 410C | Total Active Energy | 0~9999 9999.9 |  | 8454 | 2106 | Tarrif of The 3st Period | 1(Sharp) | 1：sharp，2：Peak，3：Flat，4：Valley | 14 | 8461 | 210D | 03 Read 06/10 Write |  | Start Time of The 5st Period: Hour, Minute | Unsigned 16-bit | 14:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 14 | 9997 | 270D | 03 Read 06/10 Write | Start Time of The 5th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16653 | 410D |  |  |  | 8455 | 2107 | Start Time of The 3st Period: Hour, Minute | 10:30 | High bit Hour:0~23 Low bit Minute:0~59 | 15 | 8462 | 210E | 03 Read 06/10 Write |  | End Time of The 5st Period: Hour, Minute | Unsigned 16-bit | 15:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 15 | 9998 | 270E | 03 Read 06/10 Write | End Time of The 5th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16654 | 410E | Import Active Energy | 0~9999 9999.9 |  | 8456 | 2108 | End Time of The 3st Period: Hour, Minute | 11:30 | High bit Hour:0~23 Low bit Minute:0~59 | 16 | 8463 | 210F | 03 Read 06/10 Write |  | Rate of The 6st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 16 | 9999 | 270F | 03 Read 06/10 Write | Rate of The 6th Month Period | Unsigned 16-bit | 0 | refer to Multi rate Time Period Table 1/2/3/5 | ——
| 16655 | 410F |  |  |  | 8457 | 2109 | Tarrif of The 4st Period | 3(Flat） | 1：sharp，2：Peak，3：Flat，4：Valley | 17 | 8464 | 2110 | 03 Read 06/10 Write |  | Start Time of The 6st Period: Hour, Minute | Unsigned 16-bit | 22:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 17 | 10000 | 2710 | 03 Read 06/10 Write | Start Time of The 6th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16656 | 4110 | Export Active Energy | 0~9999 9999.9 |  | 8458 | 210A | Start Time of The 4st Period: Hour, Minute | 11:30 | High bit Hour:0~23 Low bit Minute:0~59 | 18 | 8465 | 2111 | 03 Read 06/10 Write |  | End Time of The 6st Period: Hour, Minute | Unsigned 16-bit | 0:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 18 | 10001 | 2711 | 03 Read 06/10 Write | End Time of The 6th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16657 | 4111 |  |  |  | 8459 | 210B | End Time of The 4st Period: Hour, Minute | 16:00 | High bit Hour:0~23 Low bit Minute:0~59 | 19 | 8466 | 2112 | 03 Read 06/10 Write |  | Rate of The 7st Period | Unsigned 16-bit | 4 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 19 | 10002 | 2712 | 03 Read 06/10 Write | Rate of The 7th Month Period | Unsigned 16-bit | 0 | refer to Multi rate Time Period Table 1/2/3/6 | ——
| 16658 | 4112 | Total Reactive Energy | 0~9999 9999.9 |  | 8460 | 210C | Tarrif of The 5st Period | 2 (Peak) | 1：sharp，2：Peak，3：Flat，4：Valley | 20 | 8467 | 2113 | 03 Read 06/10 Write |  | Start Time of The 7st Period: Hour, Minute | Unsigned 16-bit | 0:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 20 | 10003 | 2713 | 03 Read 06/10 Write | Start Time of The 7th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16659 | 4113 |  |  |  | 8461 | 210D | Start Time of The 5st Period: Hour, Minute | 16:00 | High bit Hour:0~23 Low bit Minute:0~59 | 21 | 8468 | 2114 | 03 Read 06/10 Write |  | End Time of The 7st Period: Hour, Minute | Unsigned 16-bit | 7:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 21 | 10004 | 2714 | 03 Read 06/10 Write | End Time of The 7th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16660 | 4114 | Import Reactive Energy | 0~9999 9999.9 |  | 8462 | 210E | End Time of The 5st Period: Hour, Minute | 19:00 | High bit Hour:0~23 Low bit Minute:0~59 | 22 | 8469 | 2115 | 03 Read 06/10 Write |  | Rate of The 8st Period | Unsigned 16-bit | 4 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 22 | 10005 | 2715 | 03 Read 06/10 Write | Rate of The 8th Month Period | Unsigned 16-bit | 0 | refer to Multi rate Time Period Table 1/2/3/7 | ——
| 16661 | 4115 |  |  |  | 8463 | 210F | Tarrif of The 6st Period | 1(Sharp) | 1：sharp，2：Peak，3：Flat，4：Valley | 23 | 8470 | 2116 | 03 Read 06/10 Write |  | Start Time of The 8st Period: Hour, Minute | Unsigned 16-bit | 12:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 23 | 10006 | 2716 | 03 Read 06/10 Write | Start Time of The 8th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16662 | 4116 | Export Reactive Energy | 0~9999 9999.9 |  | 8464 | 2110 | Start Time of The 6st Period: Hour, Minute | 19:00 | High bit Hour:0~23 Low bit Minute:0~59 | 24 | 8471 | 2117 | 03 Read 06/10 Write |  | End Time of The 8st Period: Hour, Minute | Unsigned 16-bit | 14:00 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 24 | 10007 | 2717 | 03 Read 06/10 Write | End Time of The 8th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16663 | 4117 |  |  |  | 8465 | 2111 | End Time of The 6st Period: Hour, Minute | 21:00 | High bit Hour:0~23 Low bit Minute:0~59 | 25 | 8472 | 2118 | 03 Read 06/10 Write |  | Rate of The 9st Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 25 | 10008 | 2718 | 03 Read 06/10 Write | Rate of The 9th Month Period | Unsigned 16-bit | 0 | refer to Multi rate Time Period Table 1/2/3/8 | ——
Present-month Energy (Peak-period Energy) | 16664 | 4118 | Total Active Energy | 0~9999 9999.9 |  | 8466 | 2112 | Tarrif of The 7st Period | 3(Flat） | 1：sharp，2：Peak，3：Flat，4：Valley | 26 | 8473 | 2119 | 03 Read 06/10 Write |  | Start Time of The 9st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 26 | 10009 | 2719 | 03 Read 06/10 Write | Start Time of The 9th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16665 | 4119 |  |  |  | 8467 | 2113 | Start Time of The 7st Period: Hour, Minute | 21:00 | High bit Hour:0~23 Low bit Minute:0~59 | 27 | 8474 | 211A | 03 Read 06/10 Write |  | End Time of The 9st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 27 | 10010 | 271A | 03 Read 06/10 Write | End Time of The 9th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16666 | 411A | Import Active Energy | 0~9999 9999.9 |  | 8468 | 2114 | End Time of The 7st Period: Hour, Minute | 23:00 | High bit Hour:0~23 Low bit Minute:0~59 | 28 | 8475 | 211B | 03 Read 06/10 Write |  | Rate of The 10st Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 28 | 10011 | 271B | 03 Read 06/10 Write | Rate of The 10th Month Period | Unsigned 16-bit | 0 | refer to Multi rate Time Period Table 1/2/3/9 | ——
| 16667 | 411B |  |  |  | 8469 | 2115 | Tarrif of The 8st Period | 4(Valley) | 1：sharp，2：Peak，3：Flat，4：Valley | 29 | 8476 | 211C | 03 Read 06/10 Write |  | Start Time of The 10st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 29 | 10012 | 271C | 03 Read 06/10 Write | Start Time of The 10th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16668 | 411C | Export Active Energy | 0~9999 9999.9 |  | 8470 | 2116 | Start Time of The 8st Period: Hour, Minute | 23:00 | High bit Hour:0~23 Low bit Minute:0~59 | 30 | 8477 | 211D | 03 Read 06/10 Write |  | End Time of The 10st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 30 | 10013 | 271D | 03 Read 06/10 Write | End Time of The 10th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16669 | 411D |  |  |  | 8471 | 2117 | End Time of The 8st Period: Hour, Minute | 7:00 | High bit Hour:0~23 Low bit Minute:0~59 | 31 | 8478 | 211E | 03 Read 06/10 Write |  | Rate of The 11th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 31 | 10014 | 271E | 03 Read 06/10 Write | Rate of The 11th Month Period | Unsigned 16-bit | 0 | refer to Multi rate Time Period Table 1/2/3/10 | ——
| 16670 | 411E | Total Reactive Energy | 0~9999 9999.9 |  | 8472 | 2118 | Tarrif of The 9st Period | 0 | 1：sharp，2：Peak，3：Flat，4：Valley | 32 | 8479 | 211F | 03 Read 06/10 Write |  | Start Time of The 11th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 32 | 10015 | 271F | 03 Read 06/10 Write | Start Time of The 11th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16671 | 411F |  |  |  | 8473 | 2119 | Start Time of The 9st Period: Hour, Minute | 0:00 | High bit Hour:0~23 Low bit Minute:0~59 | 33 | 8480 | 2120 | 03 Read 06/10 Write |  | End Time of The 11th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 33 | 10016 | 2720 | 03 Read 06/10 Write | End Time of The 11th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16672 | 4120 | Import Reactive Energy | 0~9999 9999.9 |  | 8474 | 211A | End Time of The 9st Period: Hour, Minute | 0:00 | High bit Hour:0~23 Low bit Minute:0~59 | 34 | 8481 | 2121 | 03 Read 06/10 Write |  | Rate of The 12th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 34 | 10017 | 2721 | 03 Read 06/10 Write | Rate of The 12th Month Period | Unsigned 16-bit | 0 | refer to Multi rate Time Period Table 1/2/3/11 | ——
| 16673 | 4121 |  |  |  | 8475 | 211B | Tarrif of The 10st Period | 0 | 1：sharp，2：Peak，3：Flat，4：Valley | 35 | 8482 | 2122 | 03 Read 06/10 Write |  | Start Time of The 12th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 35 | 10018 | 2722 | 03 Read 06/10 Write | Start Time of The 12th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16674 | 4122 | Export Reactive Energy | 0~9999 9999.9 |  | 8476 | 211C | Start Time of The 10st Period: Hour, Minute | 0:00 | High bit Hour:0~23 Low bit Minute:0~59 | 36 | 8483 | 2123 | 03 Read 06/10 Write |  | End Time of The 12th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 36 | 10019 | 2723 | 03 Read 06/10 Write | End Time of The 12th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16675 | 4123 |  |  |  | 8477 | 211D | End Time of The 10st Period: Hour, Minute | 0:00 | High bit Hour:0~23 Low bit Minute:0~59 | 37 | 8484 | 2124 | 03 Read 06/10 Write |  | Rate of The 13th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 37 | 10020 | 2724 | 03 Read 06/10 Write | Rate of The 13th Month Period | Unsigned 16-bit | 0 | refer to Multi rate Time Period Table 1/2/3/12 | ——
Present-month Energy (Flat-period Energy) | 16676 | 4124 | Total Active Energy | 0~9999 9999.9 | [6 empty] | 38 | 8485 | 2125 | 03 Read 06/10 Write |  | Start Time of The 13th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 38 | 10021 | 2725 | 03 Read 06/10 Write | Start Time of The 13th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16677 | 4125 | [8 empty] | 39 | 8486 | 2126 | 03 Read 06/10 Write |  | End Time of The 13th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 39 | 10022 | 2726 | 03 Read 06/10 Write | End Time of The 13th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16678 | 4126 | Import Active Energy | 0~9999 9999.9 | [6 empty] | 40 | 8487 | 2127 | 03 Read 06/10 Write |  | Rate of The 14th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 40 | 10023 | 2727 | 03 Read 06/10 Write | Rate of The 14th Month Period | Unsigned 16-bit | 0 | refer to Multi rate Time Period Table 1/2/3/13 | ——
| 16679 | 4127 | [8 empty] | 41 | 8488 | 2128 | 03 Read 06/10 Write |  | Start Time of The 14th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 41 | 10024 | 2728 | 03 Read 06/10 Write | Start Time of The 14th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16680 | 4128 | Export Active Energy | 0~9999 9999.9 | [6 empty] | 42 | 8489 | 2129 | 03 Read 06/10 Write |  | End Time of The 14th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 42 | 10025 | 2729 | 03 Read 06/10 Write | End Time of The 14th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16681 | 4129 | [8 empty] | 43 | 8490 | 212A | 03 Read 06/10 Write |  | Rate of The 15th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 43 | 10026 | 272A | 03 Read 06/10 Write | Rate of The 15th Month Period | Unsigned 16-bit | 0 | refer to Multi rate Time Period Table 1/2/3/14 | ——
| 16682 | 412A | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 44 | 8491 | 212B | 03 Read 06/10 Write |  | Start Time of The 15th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 44 | 10027 | 272B | 03 Read 06/10 Write | Start Time of The 15th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16683 | 412B | [8 empty] | 45 | 8492 | 212C | 03 Read 06/10 Write |  | End Time of The 15th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 45 | 10028 | 272C | 03 Read 06/10 Write | End Time of The 15th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16684 | 412C | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 46 | 8493 | 212D | 03 Read 06/10 Write |  | Rate of The 16th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | —— |  | 46 | 10029 | 272D | 03 Read 06/10 Write | Rate of The 16th Month Period | Unsigned 16-bit | 0 | refer to Multi rate Time Period Table 1/2/3/15 | ——
| 16685 | 412D | [8 empty] | 47 | 8494 | 212E | 03 Read 06/10 Write |  | Start Time of The 16th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 47 | 10030 | 272E | 03 Read 06/10 Write | Start Time of The 16th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16686 | 412E | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 48 | 8495 | 212F | 03 Read 06/10 Write |  | End Time of The 16th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | —— |  | 48 | 10031 | 272F | 03 Read 06/10 Write | End Time of The 16th Month Period: month, day | Unsigned 16-bit | 0 | High bit Month :0~12 Low bit Day :0~31 | ——
| 16687 | 412F | [8 empty] | note：The multi rate version is valid. When the time period rate is 0, the time period is not used. Unset time periods are subject to the "flat" time period rate.
Present-month Energy (Valley-period Energy) | 16688 | 4130 | Total Active Energy | 0~9999 9999.9 | [6 empty] | Multi rate Time Period Table 2
[11 empty] | No, | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
| 16689 | 4131
| 16690 | 4132 | Import Active Energy | 0~9999 9999.9 | [6 empty] | 1 | 8448 | 2100 | 03 Read 06/10 Write | Multi Tarrif Period Setting | Rate of The 1st Period | Unsigned 16-bit | 2 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16691 | 4133 | [8 empty] | 2 | 8449 | 2101 | 03 Read 06/10 Write |  | Start Time of The 1st Period: Hour, Minute | Unsigned 16-bit | 9:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16692 | 4134 | Export Active Energy | 0~9999 9999.9 | [6 empty] | 3 | 8450 | 2102 | 03 Read 06/10 Write |  | End Time of The 1st Period: Hour, Minute | Unsigned 16-bit | 11:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16693 | 4135 | [8 empty] | 4 | 8451 | 2103 | 03 Read 06/10 Write |  | Rate of The 2st Period | Unsigned 16-bit | 2 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16694 | 4136 | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 5 | 8452 | 2104 | 03 Read 06/10 Write |  | Start Time of The 2st Period: Hour, Minute | Unsigned 16-bit | 15:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16695 | 4137 | [8 empty] | 6 | 8453 | 2105 | 03 Read 06/10 Write |  | End Time of The 2st Period: Hour, Minute | Unsigned 16-bit | 22:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16696 | 4138 | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 7 | 8454 | 2106 | 03 Read 06/10 Write |  | Rate of The 3st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16697 | 4139 | [8 empty] | 8 | 8455 | 2107 | 03 Read 06/10 Write |  | Start Time of The 3st Period: Hour, Minute | Unsigned 16-bit | 07:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16698 | 413A | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 9 | 8456 | 2108 | 03 Read 06/10 Write |  | End Time of The 3st Period: Hour, Minute | Unsigned 16-bit | 09:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16699 | 413B | [8 empty] | 10 | 8457 | 2109 | 03 Read 06/10 Write |  | Rate of The 4st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
Last 1st month Energy (Total Energy) | 16700 | 413C | Total Active Energy | 0~9999 9999.9 | [6 empty] | 11 | 8458 | 210A | 03 Read 06/10 Write |  | Start Time of The 4st Period: Hour, Minute | Unsigned 16-bit | 11:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16701 | 413D | [8 empty] | 12 | 8459 | 210B | 03 Read 06/10 Write |  | End Time of The 4st Period: Hour, Minute | Unsigned 16-bit | 12:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16702 | 413E | Import Active Energy | 0~9999 9999.9 | [6 empty] | 13 | 8460 | 210C | 03 Read 06/10 Write |  | Rate of The 5st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16703 | 413F | [8 empty] | 14 | 8461 | 210D | 03 Read 06/10 Write |  | Start Time of The 5st Period: Hour, Minute | Unsigned 16-bit | 14:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16704 | 4140 | Export Active Energy | 0~9999 9999.9 | [6 empty] | 15 | 8462 | 210E | 03 Read 06/10 Write |  | End Time of The 5st Period: Hour, Minute | Unsigned 16-bit | 15:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16705 | 4141 | [8 empty] | 16 | 8463 | 210F | 03 Read 06/10 Write |  | Rate of The 6st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16706 | 4142 | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 17 | 8464 | 2110 | 03 Read 06/10 Write |  | Start Time of The 6st Period: Hour, Minute | Unsigned 16-bit | 22:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16707 | 4143 | [8 empty] | 18 | 8465 | 2111 | 03 Read 06/10 Write |  | End Time of The 6st Period: Hour, Minute | Unsigned 16-bit | 0:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16708 | 4144 | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 19 | 8466 | 2112 | 03 Read 06/10 Write |  | Rate of The 7st Period | Unsigned 16-bit | 4 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16709 | 4145 | [8 empty] | 20 | 8467 | 2113 | 03 Read 06/10 Write |  | Start Time of The 7st Period: Hour, Minute | Unsigned 16-bit | 0:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16710 | 4146 | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 21 | 8468 | 2114 | 03 Read 06/10 Write |  | End Time of The 7st Period: Hour, Minute | Unsigned 16-bit | 7:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16711 | 4147 | [8 empty] | 22 | 8469 | 2115 | 03 Read 06/10 Write |  | Rate of The 8st Period | Unsigned 16-bit | 4 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
Last 1st month Energy (Sharp-period Energy) | 16712 | 4148 | Total Active Energy | 0~9999 9999.9 | [6 empty] | 23 | 8470 | 2116 | 03 Read 06/10 Write |  | Start Time of The 8st Period: Hour, Minute | Unsigned 16-bit | 12:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16713 | 4149 | [8 empty] | 24 | 8471 | 2117 | 03 Read 06/10 Write |  | End Time of The 8st Period: Hour, Minute | Unsigned 16-bit | 14:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16714 | 414A | Import Active Energy | 0~9999 9999.9 | [6 empty] | 25 | 8472 | 2118 | 03 Read 06/10 Write |  | Rate of The 9st Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16715 | 414B | [8 empty] | 26 | 8473 | 2119 | 03 Read 06/10 Write |  | Start Time of The 9st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16716 | 414C | Export Active Energy | 0~9999 9999.9 | [6 empty] | 27 | 8474 | 211A | 03 Read 06/10 Write |  | End Time of The 9st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16717 | 414D | [8 empty] | 28 | 8475 | 211B | 03 Read 06/10 Write |  | Rate of The 10st Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16718 | 414E | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 29 | 8476 | 211C | 03 Read 06/10 Write |  | Start Time of The 10st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16719 | 414F | [8 empty] | 30 | 8477 | 211D | 03 Read 06/10 Write |  | End Time of The 10st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16720 | 4150 | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 31 | 8478 | 211E | 03 Read 06/10 Write |  | Rate of The 11th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16721 | 4151 | [8 empty] | 32 | 8479 | 211F | 03 Read 06/10 Write |  | Start Time of The 11th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16722 | 4152 | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 33 | 8480 | 2120 | 03 Read 06/10 Write |  | End Time of The 11th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16723 | 4153 | [8 empty] | 34 | 8481 | 2121 | 03 Read 06/10 Write |  | Rate of The 12th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
Last 1st month Energy (Peak-period Energy) | 16724 | 4154 | Total Active Energy | 0~9999 9999.9 | [6 empty] | 35 | 8482 | 2122 | 03 Read 06/10 Write |  | Start Time of The 12th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16725 | 4155 | [8 empty] | 36 | 8483 | 2123 | 03 Read 06/10 Write |  | End Time of The 12th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16726 | 4156 | Import Active Energy | 0~9999 9999.9 | [6 empty] | 37 | 8484 | 2124 | 03 Read 06/10 Write |  | Rate of The 13th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16727 | 4157 | [8 empty] | 38 | 8485 | 2125 | 03 Read 06/10 Write |  | Start Time of The 13th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16728 | 4158 | Export Active Energy | 0~9999 9999.9 | [6 empty] | 39 | 8486 | 2126 | 03 Read 06/10 Write |  | End Time of The 13th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16729 | 4159 | [8 empty] | 40 | 8487 | 2127 | 03 Read 06/10 Write |  | Rate of The 14th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16730 | 415A | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 41 | 8488 | 2128 | 03 Read 06/10 Write |  | Start Time of The 14th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16731 | 415B | [8 empty] | 42 | 8489 | 2129 | 03 Read 06/10 Write |  | End Time of The 14th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16732 | 415C | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 43 | 8490 | 212A | 03 Read 06/10 Write |  | Rate of The 15th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16733 | 415D | [8 empty] | 44 | 8491 | 212B | 03 Read 06/10 Write |  | Start Time of The 15th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16734 | 415E | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 45 | 8492 | 212C | 03 Read 06/10 Write |  | End Time of The 15th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16735 | 415F | [8 empty] | 46 | 8493 | 212D | 03 Read 06/10 Write |  | Rate of The 16th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
Last 1st month Energy (Flat-period Energy) | 16736 | 4160 | Total Active Energy | 0~9999 9999.9 | [6 empty] | 47 | 8494 | 212E | 03 Read 06/10 Write |  | Start Time of The 16th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16737 | 4161 | [8 empty] | 48 | 8495 | 212F | 03 Read 06/10 Write |  | End Time of The 16th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16738 | 4162 | Import Active Energy | 0~9999 9999.9 | [6 empty] | note：The multi rate version is valid. When the time period rate is 0, the time period is not used. Unset time periods are subject to the "flat" time period rate.
| 16739 | 4163 | [8 empty] | Multi rate Time Period Table 3
[11 empty] | No, | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
| 16740 | 4164 | Export Active Energy | 0~9999 9999.9
| 16741 | 4165 | [8 empty] | 1 | 8448 | 2100 | 03 Read 06/10 Write | Multi Tarrif Period Setting | Rate of The 1st Period | Unsigned 16-bit | 2 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16742 | 4166 | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 2 | 8449 | 2101 | 03 Read 06/10 Write |  | Start Time of The 1st Period: Hour, Minute | Unsigned 16-bit | 9:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16743 | 4167 | [8 empty] | 3 | 8450 | 2102 | 03 Read 06/10 Write |  | End Time of The 1st Period: Hour, Minute | Unsigned 16-bit | 11:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16744 | 4168 | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 4 | 8451 | 2103 | 03 Read 06/10 Write |  | Rate of The 2st Period | Unsigned 16-bit | 2 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16745 | 4169 | [8 empty] | 5 | 8452 | 2104 | 03 Read 06/10 Write |  | Start Time of The 2st Period: Hour, Minute | Unsigned 16-bit | 15:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16746 | 416A | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 6 | 8453 | 2105 | 03 Read 06/10 Write |  | End Time of The 2st Period: Hour, Minute | Unsigned 16-bit | 22:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16747 | 416B | [8 empty] | 7 | 8454 | 2106 | 03 Read 06/10 Write |  | Rate of The 3st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
Last 1st month Energy (Valley-period Energy) | 16748 | 416C | Total Active Energy | 0~9999 9999.9 | [6 empty] | 8 | 8455 | 2107 | 03 Read 06/10 Write |  | Start Time of The 3st Period: Hour, Minute | Unsigned 16-bit | 07:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16749 | 416D | [8 empty] | 9 | 8456 | 2108 | 03 Read 06/10 Write |  | End Time of The 3st Period: Hour, Minute | Unsigned 16-bit | 09:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16750 | 416E | Import Active Energy | 0~9999 9999.9 | [6 empty] | 10 | 8457 | 2109 | 03 Read 06/10 Write |  | Rate of The 4st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16751 | 416F | [8 empty] | 11 | 8458 | 210A | 03 Read 06/10 Write |  | Start Time of The 4st Period: Hour, Minute | Unsigned 16-bit | 11:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16752 | 4170 | Export Active Energy | 0~9999 9999.9 | [6 empty] | 12 | 8459 | 210B | 03 Read 06/10 Write |  | End Time of The 4st Period: Hour, Minute | Unsigned 16-bit | 12:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16753 | 4171 | [8 empty] | 13 | 8460 | 210C | 03 Read 06/10 Write |  | Rate of The 5st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16754 | 4172 | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 14 | 8461 | 210D | 03 Read 06/10 Write |  | Start Time of The 5st Period: Hour, Minute | Unsigned 16-bit | 14:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16755 | 4173 | [8 empty] | 15 | 8462 | 210E | 03 Read 06/10 Write |  | End Time of The 5st Period: Hour, Minute | Unsigned 16-bit | 15:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16756 | 4174 | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 16 | 8463 | 210F | 03 Read 06/10 Write |  | Rate of The 6st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16757 | 4175 | [8 empty] | 17 | 8464 | 2110 | 03 Read 06/10 Write |  | Start Time of The 6st Period: Hour, Minute | Unsigned 16-bit | 22:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16758 | 4176 | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 18 | 8465 | 2111 | 03 Read 06/10 Write |  | End Time of The 6st Period: Hour, Minute | Unsigned 16-bit | 0:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16759 | 4177 | [8 empty] | 19 | 8466 | 2112 | 03 Read 06/10 Write |  | Rate of The 7st Period | Unsigned 16-bit | 4 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
Last 2st month Energy (Total Energy) | 16760 | 4178 | Total Active Energy | 0~9999 9999.9 | [6 empty] | 20 | 8467 | 2113 | 03 Read 06/10 Write |  | Start Time of The 7st Period: Hour, Minute | Unsigned 16-bit | 0:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16761 | 4179 | [8 empty] | 21 | 8468 | 2114 | 03 Read 06/10 Write |  | End Time of The 7st Period: Hour, Minute | Unsigned 16-bit | 7:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16762 | 417A | Import Active Energy | 0~9999 9999.9 | [6 empty] | 22 | 8469 | 2115 | 03 Read 06/10 Write |  | Rate of The 8st Period | Unsigned 16-bit | 4 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16763 | 417B | [8 empty] | 23 | 8470 | 2116 | 03 Read 06/10 Write |  | Start Time of The 8st Period: Hour, Minute | Unsigned 16-bit | 12:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16764 | 415C | Export Active Energy | 0~9999 9999.9 | [6 empty] | 24 | 8471 | 2117 | 03 Read 06/10 Write |  | End Time of The 8st Period: Hour, Minute | Unsigned 16-bit | 14:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16765 | 417D | [8 empty] | 25 | 8472 | 2118 | 03 Read 06/10 Write |  | Rate of The 9st Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16766 | 417E | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 26 | 8473 | 2119 | 03 Read 06/10 Write |  | Start Time of The 9st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16767 | 417F | [8 empty] | 27 | 8474 | 211A | 03 Read 06/10 Write |  | End Time of The 9st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16768 | 4180 | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 28 | 8475 | 211B | 03 Read 06/10 Write |  | Rate of The 10st Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16769 | 4181 | [8 empty] | 29 | 8476 | 211C | 03 Read 06/10 Write |  | Start Time of The 10st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16770 | 4182 | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 30 | 8477 | 211D | 03 Read 06/10 Write |  | End Time of The 10st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16771 | 4183 | [8 empty] | 31 | 8478 | 211E | 03 Read 06/10 Write |  | Rate of The 11th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
Last 2st month Energy (Sharp-period Energy) | 16772 | 4184 | Total Active Energy | 0~9999 9999.9 | [6 empty] | 32 | 8479 | 211F | 03 Read 06/10 Write |  | Start Time of The 11th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16773 | 4185 | [8 empty] | 33 | 8480 | 2120 | 03 Read 06/10 Write |  | End Time of The 11th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16774 | 4186 | Import Active Energy | 0~9999 9999.9 | [6 empty] | 34 | 8481 | 2121 | 03 Read 06/10 Write |  | Rate of The 12th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16775 | 4187 | [8 empty] | 35 | 8482 | 2122 | 03 Read 06/10 Write |  | Start Time of The 12th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16776 | 4188 | Export Active Energy | 0~9999 9999.9 | [6 empty] | 36 | 8483 | 2123 | 03 Read 06/10 Write |  | End Time of The 12th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16777 | 4189 | [8 empty] | 37 | 8484 | 2124 | 03 Read 06/10 Write |  | Rate of The 13th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16778 | 418A | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 38 | 8485 | 2125 | 03 Read 06/10 Write |  | Start Time of The 13th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16779 | 418B | [8 empty] | 39 | 8486 | 2126 | 03 Read 06/10 Write |  | End Time of The 13th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16780 | 418C | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 40 | 8487 | 2127 | 03 Read 06/10 Write |  | Rate of The 14th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16781 | 418D | [8 empty] | 41 | 8488 | 2128 | 03 Read 06/10 Write |  | Start Time of The 14th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16782 | 418E | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 42 | 8489 | 2129 | 03 Read 06/10 Write |  | End Time of The 14th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16783 | 418F | [8 empty] | 43 | 8490 | 212A | 03 Read 06/10 Write |  | Rate of The 15th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
Last 2st month Energy (Peak-period Energy) | 16784 | 4190 | Total Active Energy | 0~9999 9999.9 | [6 empty] | 44 | 8491 | 212B | 03 Read 06/10 Write |  | Start Time of The 15th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16785 | 4191 | [8 empty] | 45 | 8492 | 212C | 03 Read 06/10 Write |  | End Time of The 15th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16786 | 4192 | Import Active Energy | 0~9999 9999.9 | [6 empty] | 46 | 8493 | 212D | 03 Read 06/10 Write |  | Rate of The 16th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16787 | 4193 | [8 empty] | 47 | 8494 | 212E | 03 Read 06/10 Write |  | Start Time of The 16th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16788 | 4194 | Export Active Energy | 0~9999 9999.9 | [6 empty] | 48 | 8495 | 212F | 03 Read 06/10 Write |  | End Time of The 16th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16789 | 4195 | [8 empty] | note：The multi rate version is valid. When the time period rate is 0, the time period is not used. Unset time periods are subject to the "flat" time period rate.
| 16790 | 4196 | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | Multi rate Time Period Table 4
| 16791 | 4197 | [8 empty] | No, | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
| 16792 | 4198 | Import Reactive Energy | 0~9999 9999.9
| 16793 | 4199 | [8 empty] | 1 | 8448 | 2100 | 03 Read 06/10 Write | Multi Tarrif Period Setting | Rate of The 1st Period | Unsigned 16-bit | 2 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16794 | 419A | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 2 | 8449 | 2101 | 03 Read 06/10 Write |  | Start Time of The 1st Period: Hour, Minute | Unsigned 16-bit | 9:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16795 | 419B | [8 empty] | 3 | 8450 | 2102 | 03 Read 06/10 Write |  | End Time of The 1st Period: Hour, Minute | Unsigned 16-bit | 11:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
Last 2st month Energy (Flat-period Energy) | 16796 | 419C | Total Active Energy | 0~9999 9999.9 | [6 empty] | 4 | 8451 | 2103 | 03 Read 06/10 Write |  | Rate of The 2st Period | Unsigned 16-bit | 2 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16797 | 419D | [8 empty] | 5 | 8452 | 2104 | 03 Read 06/10 Write |  | Start Time of The 2st Period: Hour, Minute | Unsigned 16-bit | 15:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16798 | 419E | Import Active Energy | 0~9999 9999.9 | [6 empty] | 6 | 8453 | 2105 | 03 Read 06/10 Write |  | End Time of The 2st Period: Hour, Minute | Unsigned 16-bit | 22:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16799 | 419F | [8 empty] | 7 | 8454 | 2106 | 03 Read 06/10 Write |  | Rate of The 3st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16800 | 41A0 | Export Active Energy | 0~9999 9999.9 | [6 empty] | 8 | 8455 | 2107 | 03 Read 06/10 Write |  | Start Time of The 3st Period: Hour, Minute | Unsigned 16-bit | 07:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16801 | 41A1 | [8 empty] | 9 | 8456 | 2108 | 03 Read 06/10 Write |  | End Time of The 3st Period: Hour, Minute | Unsigned 16-bit | 09:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16802 | 41A2 | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 10 | 8457 | 2109 | 03 Read 06/10 Write |  | Rate of The 4st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16803 | 41A3 | [8 empty] | 11 | 8458 | 210A | 03 Read 06/10 Write |  | Start Time of The 4st Period: Hour, Minute | Unsigned 16-bit | 11:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16804 | 41A4 | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 12 | 8459 | 210B | 03 Read 06/10 Write |  | End Time of The 4st Period: Hour, Minute | Unsigned 16-bit | 12:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16805 | 41A5 | [8 empty] | 13 | 8460 | 210C | 03 Read 06/10 Write |  | Rate of The 5st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16806 | 41A6 | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 14 | 8461 | 210D | 03 Read 06/10 Write |  | Start Time of The 5st Period: Hour, Minute | Unsigned 16-bit | 14:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16807 | 41A7 | [8 empty] | 15 | 8462 | 210E | 03 Read 06/10 Write |  | End Time of The 5st Period: Hour, Minute | Unsigned 16-bit | 15:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
Last 2st month Energy (Valley-period Energy) | 16808 | 41A8 | Total Active Energy | 0~9999 9999.9 | [6 empty] | 16 | 8463 | 210F | 03 Read 06/10 Write |  | Rate of The 6st Period | Unsigned 16-bit | 3 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16809 | 41A9 | [8 empty] | 17 | 8464 | 2110 | 03 Read 06/10 Write |  | Start Time of The 6st Period: Hour, Minute | Unsigned 16-bit | 22:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16810 | 41AA | Import Active Energy | 0~9999 9999.9 | [6 empty] | 18 | 8465 | 2111 | 03 Read 06/10 Write |  | End Time of The 6st Period: Hour, Minute | Unsigned 16-bit | 0:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16811 | 41AB | [8 empty] | 19 | 8466 | 2112 | 03 Read 06/10 Write |  | Rate of The 7st Period | Unsigned 16-bit | 4 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16812 | 41AC | Export Active Energy | 0~9999 9999.9 | [6 empty] | 20 | 8467 | 2113 | 03 Read 06/10 Write |  | Start Time of The 7st Period: Hour, Minute | Unsigned 16-bit | 0:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16813 | 41AD | [8 empty] | 21 | 8468 | 2114 | 03 Read 06/10 Write |  | End Time of The 7st Period: Hour, Minute | Unsigned 16-bit | 7:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16814 | 41AE | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 22 | 8469 | 2115 | 03 Read 06/10 Write |  | Rate of The 8st Period | Unsigned 16-bit | 4 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16815 | 41AF | [8 empty] | 23 | 8470 | 2116 | 03 Read 06/10 Write |  | Start Time of The 8st Period: Hour, Minute | Unsigned 16-bit | 12:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16816 | 41B0 | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 24 | 8471 | 2117 | 03 Read 06/10 Write |  | End Time of The 8st Period: Hour, Minute | Unsigned 16-bit | 14:00 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16817 | 41B1 | [8 empty] | 25 | 8472 | 2118 | 03 Read 06/10 Write |  | Rate of The 9st Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16818 | 41B2 | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 26 | 8473 | 2119 | 03 Read 06/10 Write |  | Start Time of The 9st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16819 | 41B3 | [8 empty] | 27 | 8474 | 211A | 03 Read 06/10 Write |  | End Time of The 9st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
Last 3st month Energy (Total Energy) | 16820 | 41B4 | Total Active Energy | 0~9999 9999.9 | [6 empty] | 28 | 8475 | 211B | 03 Read 06/10 Write |  | Rate of The 10st Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16821 | 41B5 | [8 empty] | 29 | 8476 | 211C | 03 Read 06/10 Write |  | Start Time of The 10st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16822 | 41B6 | Import Active Energy | 0~9999 9999.9 | [6 empty] | 30 | 8477 | 211D | 03 Read 06/10 Write |  | End Time of The 10st Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16823 | 41B7 | [8 empty] | 31 | 8478 | 211E | 03 Read 06/10 Write |  | Rate of The 11th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16824 | 41B8 | Export Active Energy | 0~9999 9999.9 | [6 empty] | 32 | 8479 | 211F | 03 Read 06/10 Write |  | Start Time of The 11th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16825 | 41B9 | [8 empty] | 33 | 8480 | 2120 | 03 Read 06/10 Write |  | End Time of The 11th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16826 | 41BA | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 34 | 8481 | 2121 | 03 Read 06/10 Write |  | Rate of The 12th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16827 | 41BB | [8 empty] | 35 | 8482 | 2122 | 03 Read 06/10 Write |  | Start Time of The 12th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16828 | 41BC | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 36 | 8483 | 2123 | 03 Read 06/10 Write |  | End Time of The 12th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16829 | 41BD | [8 empty] | 37 | 8484 | 2124 | 03 Read 06/10 Write |  | Rate of The 13th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16830 | 41BE | Export Reactive Energy | 0~9999 9999.9 | [6 empty] | 38 | 8485 | 2125 | 03 Read 06/10 Write |  | Start Time of The 13th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16831 | 41BF | [8 empty] | 39 | 8486 | 2126 | 03 Read 06/10 Write |  | End Time of The 13th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
Last 3st month Energy (Sharp-period Energy) | 16832 | 41C0 | Total Active Energy | 0~9999 9999.9 | [6 empty] | 40 | 8487 | 2127 | 03 Read 06/10 Write |  | Rate of The 14th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16833 | 41C1 | [8 empty] | 41 | 8488 | 2128 | 03 Read 06/10 Write |  | Start Time of The 14th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16834 | 41C2 | Import Active Energy | 0~9999 9999.9 | [6 empty] | 42 | 8489 | 2129 | 03 Read 06/10 Write |  | End Time of The 14th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16835 | 41C3 | [8 empty] | 43 | 8490 | 212A | 03 Read 06/10 Write |  | Rate of The 15th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16836 | 41C4 | Export Active Energy | 0~9999 9999.9 | [6 empty] | 44 | 8491 | 212B | 03 Read 06/10 Write |  | Start Time of The 15th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16837 | 41C5 | [8 empty] | 45 | 8492 | 212C | 03 Read 06/10 Write |  | End Time of The 15th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16838 | 41C6 | Total Reactive Energy | 0~9999 9999.9 | [6 empty] | 46 | 8493 | 212D | 03 Read 06/10 Write |  | Rate of The 16th Period | Unsigned 16-bit | 0 | 1：sharp， 2：Peak， 3：Flat， 4：Valley , 5:Deep Valley | ——
| 16839 | 41C7 | [8 empty] | 47 | 8494 | 212E | 03 Read 06/10 Write |  | Start Time of The 16th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16840 | 41C8 | Import Reactive Energy | 0~9999 9999.9 | [6 empty] | 48 | 8495 | 212F | 03 Read 06/10 Write |  | End Time of The 16th Period: Hour, Minute | Unsigned 16-bit | 0 | High bit Hour:0~23 Low bit Minute:0~59 | ——
| 16841 | 41C9 | [8 empty] | note：The multi rate version is valid. When the time period rate is 0, the time period is not used. Unset time periods are subject to the "flat" time period rate.
| 16842 | 41CA | Export Reactive Energy | 0~9999 9999.9
| 16843 | 41CB
Last 3st month Energy (Peak-period Energy) | 16844 | 41CC | Total Active Energy | 0~9999 9999.9
| 16845 | 41CD
| 16846 | 41CE | Import Active Energy | 0~9999 9999.9
| 16847 | 41CF
| 16848 | 41D0 | Export Active Energy | 0~9999 9999.9
| 16849 | 41D1
| 16850 | 41D2 | Total Reactive Energy | 0~9999 9999.9
| 16851 | 41D3
| 16852 | 41D4 | Import Reactive Energy | 0~9999 9999.9
| 16853 | 41D5
| 16854 | 41D6 | Export Reactive Energy | 0~9999 9999.9
| 16855 | 41D7
Last 3st month Energy (Flat-period Energy) | 16856 | 41D8 | Total Active Energy | 0~9999 9999.9
| 16857 | 41D9
| 16858 | 41DA | Import Active Energy | 0~9999 9999.9
| 16859 | 41DB
| 16860 | 41DC | Export Active Energy | 0~9999 9999.9
| 16861 | 41DD
| 16862 | 41DE | Total Reactive Energy | 0~9999 9999.9
| 16863 | 41DF
| 16864 | 41 | Import Reactive Energy | 0~9999 9999.9
| 16865 | 410
| 16866 | 4100 | Export Reactive Energy | 0~9999 9999.9
| 16867 | 41000
Last 3st month Energy (Valley-period Energy) | 16868 | 410000 | Total Active Energy | 0~9999 9999.9
| 16869 | 4100000
| 16870 | 41000000 | Import Active Energy | 0~9999 9999.9
| 16871 | 410000000
| 16872 | 4100000000 | Export Active Energy | 0~9999 9999.9
| 16873 | 41000000000
| 16874 | 41EA | Total Reactive Energy | 0~9999 9999.9
| 16875 | 41EB
| 16876 | 41EC | Import Reactive Energy | 0~9999 9999.9
| 16877 | 41ED
| 16878 | 41EE | Export Reactive Energy | 0~9999 9999.9
| 16879 | 41EF
Last 4st month Energy (Total Energy) | 16880 | 41F0 | Total Active Energy | 0~9999 9999.9
| 16881 | 41F1
| 16882 | 41F2 | Import Active Energy | 0~9999 9999.9
| 16883 | 41F3
| 16884 | 41F4 | Export Active Energy | 0~9999 9999.9
| 16885 | 41F5
| 16886 | 41F6 | Total Reactive Energy | 0~9999 9999.9
| 16887 | 41F7
| 16888 | 41F8 | Import Reactive Energy | 0~9999 9999.9
| 16889 | 41F9
| 16890 | 41FA | Export Reactive Energy | 0~9999 9999.9
| 16891 | 41FB
Last 4st month Energy (Sharp-period Energy) | 16892 | 41FC | Total Active Energy | 0~9999 9999.9
| 16893 | 41FD
| 16894 | 41FE | Import Active Energy | 0~9999 9999.9
| 16895 | 41FF
| 16896 | 4200 | Export Active Energy | 0~9999 9999.9
| 16897 | 4201
| 16898 | 4202 | Total Reactive Energy | 0~9999 9999.9
| 16899 | 4203
| 16900 | 4204 | Import Reactive Energy | 0~9999 9999.9
| 16901 | 4205
| 16902 | 4206 | Export Reactive Energy | 0~9999 9999.9
| 16903 | 4207
Last 4st month Energy (Peak-period Energy) | 16904 | 4208 | Total Active Energy | 0~9999 9999.9
| 16905 | 4209
| 16906 | 420A | Import Active Energy | 0~9999 9999.9
| 16907 | 420B
| 16908 | 420C | Export Active Energy | 0~9999 9999.9
| 16909 | 420D
| 16910 | 420E | Total Reactive Energy | 0~9999 9999.9
| 16911 | 420F
| 16912 | 4210 | Import Reactive Energy | 0~9999 9999.9
| 16913 | 4211
| 16914 | 4212 | Export Reactive Energy | 0~9999 9999.9
| 16915 | 4213
Last 4st month Energy (Flat-period Energy) | 16916 | 4214 | Total Active Energy | 0~9999 9999.9
| 16917 | 4215
| 16918 | 4216 | Import Active Energy | 0~9999 9999.9
| 16919 | 4217
| 16920 | 4218 | Export Active Energy | 0~9999 9999.9
| 16921 | 4219
| 16922 | 421A | Total Reactive Energy | 0~9999 9999.9
| 16923 | 421B
| 16924 | 421C | Import Reactive Energy | 0~9999 9999.9
| 16925 | 421D
| 16926 | 421E | Export Reactive Energy | 0~9999 9999.9
| 16927 | 421F
Last 4st month Energy (Valley-period Energy) | 16928 | 4220 | Total Active Energy | 0~9999 9999.9
| 16929 | 4221
| 16930 | 4222 | Import Active Energy | 0~9999 9999.9
| 16931 | 4223
| 16932 | 4224 | Export Active Energy | 0~9999 9999.9
| 16933 | 4225
| 16934 | 4226 | Total Reactive Energy | 0~9999 9999.9
| 16935 | 4227
| 16936 | 4228 | Import Reactive Energy | 0~9999 9999.9
| 16937 | 4229
| 16938 | 422A | Export Reactive Energy | 0~9999 9999.9
| 16939 | 422B
Last 5st month Energy (Total Energy) | 16940 | 422C | Total Active Energy | 0~9999 9999.9
| 16941 | 422D
| 16942 | 422E | Import Active Energy | 0~9999 9999.9
| 16943 | 422F
| 16944 | 4230 | Export Active Energy | 0~9999 9999.9
| 16945 | 4231
| 16946 | 4232 | Total Reactive Energy | 0~9999 9999.9
| 16947 | 4233
| 16948 | 4234 | Import Reactive Energy | 0~9999 9999.9
| 16949 | 4235
| 16950 | 4236 | Export Reactive Energy | 0~9999 9999.9
| 16951 | 4237
Last 5st month Energy (Sharp-period Energy) | 16952 | 4238 | Total Active Energy | 0~9999 9999.9
| 16953 | 4239
| 16954 | 423A | Import Active Energy | 0~9999 9999.9
| 16955 | 423B
| 16956 | 423C | Export Active Energy | 0~9999 9999.9
| 16957 | 423D
| 16958 | 423E | Total Reactive Energy | 0~9999 9999.9
| 16959 | 423F
| 16960 | 4240 | Import Reactive Energy | 0~9999 9999.9
| 16961 | 4241
| 16962 | 4242 | Export Reactive Energy | 0~9999 9999.9
| 16963 | 4243
Last 5st month Energy (Peak-period Energy) | 16964 | 4244 | Total Active Energy | 0~9999 9999.9
| 16965 | 4245
| 16966 | 4246 | Import Active Energy | 0~9999 9999.9
| 16967 | 4247
| 16968 | 4248 | Export Active Energy | 0~9999 9999.9
| 16969 | 4249
| 16970 | 424A | Total Reactive Energy | 0~9999 9999.9
| 16971 | 424B
| 16972 | 424C | Import Reactive Energy | 0~9999 9999.9
| 16973 | 424D
| 16974 | 424E | Export Reactive Energy | 0~9999 9999.9
| 16975 | 424F
Last 5st month Energy (Flat-period Energy) | 16976 | 4250 | Total Active Energy | 0~9999 9999.9
| 16977 | 4251
| 16978 | 4252 | Import Active Energy | 0~9999 9999.9
| 16979 | 4253
| 16980 | 4254 | Export Active Energy | 0~9999 9999.9
| 16981 | 4255
| 16982 | 4256 | Total Reactive Energy | 0~9999 9999.9
| 16983 | 4257
| 16984 | 4258 | Import Reactive Energy | 0~9999 9999.9
| 16985 | 4259
| 16986 | 425A | Export Reactive Energy | 0~9999 9999.9
| 16987 | 425B
Last 5st month Energy (Valley-period Energy) | 16988 | 425C | Total Active Energy | 0~9999 9999.9
| 16989 | 425D
| 16990 | 425E | Import Active Energy | 0~9999 9999.9
| 16991 | 425F
| 16992 | 4260 | Export Active Energy | 0~9999 9999.9
| 16993 | 4261
| 16994 | 4262 | Total Reactive Energy | 0~9999 9999.9
| 16995 | 4263
| 16996 | 4264 | Import Reactive Energy | 0~9999 9999.9
| 16997 | 4265
| 16998 | 4266 | Export Reactive Energy | 0~9999 9999.9
| 16999 | 4267
Last 6st month Energy (Total Energy) | 17000 | 4268 | Total Active Energy | 0~9999 9999.9
| 17001 | 4269
| 17002 | 426A | Import Active Energy | 0~9999 9999.9
| 17003 | 426B
| 17004 | 426C | Export Active Energy | 0~9999 9999.9
| 17005 | 426D
| 17006 | 426E | Total Reactive Energy | 0~9999 9999.9
| 17007 | 426F
| 17008 | 4270 | Import Reactive Energy | 0~9999 9999.9
| 17009 | 4271
| 17010 | 4272 | Export Reactive Energy | 0~9999 9999.9
| 17011 | 4273
Last 6st month Energy (Sharp-period Energy) | 17012 | 4274 | Total Active Energy | 0~9999 9999.9
| 17013 | 4275
| 17014 | 4276 | Import Active Energy | 0~9999 9999.9
| 17015 | 4277
| 17016 | 4278 | Export Active Energy | 0~9999 9999.9
| 17017 | 4279
| 17018 | 427A | Total Reactive Energy | 0~9999 9999.9
| 17019 | 427B
| 17020 | 425C | Import Reactive Energy | 0~9999 9999.9
| 17021 | 427D
| 17022 | 427E | Export Reactive Energy | 0~9999 9999.9
| 17023 | 427F
Last 6st month Energy (Peak-period Energy) | 17024 | 4280 | Total Active Energy | 0~9999 9999.9
| 17025 | 4281
| 17026 | 4282 | Import Active Energy | 0~9999 9999.9
| 17027 | 4283
| 17028 | 4284 | Export Active Energy | 0~9999 9999.9
| 17029 | 4285
| 17030 | 4286 | Total Reactive Energy | 0~9999 9999.9
| 17031 | 4287
| 17032 | 4288 | Import Reactive Energy | 0~9999 9999.9
| 17033 | 4289
| 17034 | 428A | Export Reactive Energy | 0~9999 9999.9
| 17035 | 428B
Last 6st month Energy (Flat-period Energy) | 17036 | 428C | Total Active Energy | 0~9999 9999.9
| 17037 | 428D
| 17038 | 428E | Import Active Energy | 0~9999 9999.9
| 17039 | 428F
| 17040 | 4290 | Export Active Energy | 0~9999 9999.9
| 17041 | 4291
| 17042 | 4292 | Total Reactive Energy | 0~9999 9999.9
| 17043 | 4293
| 17044 | 4294 | Import Reactive Energy | 0~9999 9999.9
| 17045 | 4295
| 17046 | 4296 | Export Reactive Energy | 0~9999 9999.9
| 17047 | 4297
Last 6st month Energy (Valley-period Energy) | 17048 | 4298 | Total Active Energy | 0~9999 9999.9
| 17049 | 4299
| 17050 | 429A | Import Active Energy | 0~9999 9999.9
| 17051 | 429B
| 17052 | 429C | Export Active Energy | 0~9999 9999.9
| 17053 | 429D
| 17054 | 429E | Total Reactive Energy | 0~9999 9999.9
| 17055 | 429F
| 17056 | 42A0 | Import Reactive Energy | 0~9999 9999.9
| 17057 | 42A1
| 17058 | 42A2 | Export Reactive Energy | 0~9999 9999.9
| 17059 | 42A3
Last 7st month Energy (Total Energy) | 17060 | 42A4 | Total Active Energy | 0~9999 9999.9
| 17061 | 42A5
| 17062 | 42A6 | Import Active Energy | 0~9999 9999.9
| 17063 | 42A7
| 17064 | 42A8 | Export Active Energy | 0~9999 9999.9
| 17065 | 42A9
| 17066 | 42AA | Total Reactive Energy | 0~9999 9999.9
| 17067 | 42AB
| 17068 | 42AC | Import Reactive Energy | 0~9999 9999.9
| 17069 | 42AD
| 17070 | 42AE | Export Reactive Energy | 0~9999 9999.9
| 17071 | 42AF
Last 7st month Energy (Sharp-period Energy) | 17072 | 42B0 | Total Active Energy | 0~9999 9999.9
| 17073 | 42B1
| 17074 | 42B2 | Import Active Energy | 0~9999 9999.9
| 17075 | 42B3
| 17076 | 42B4 | Export Active Energy | 0~9999 9999.9
| 17077 | 42B5
| 17078 | 42B6 | Total Reactive Energy | 0~9999 9999.9
| 17079 | 42B7
| 17080 | 42B8 | Import Reactive Energy | 0~9999 9999.9
| 17081 | 42B9
| 17082 | 42BA | Export Reactive Energy | 0~9999 9999.9
| 17083 | 42BB
Last 7st month Energy (Peak-period Energy) | 17084 | 42BC | Total Active Energy | 0~9999 9999.9
| 17085 | 42BD
| 17086 | 42BE | Import Active Energy | 0~9999 9999.9
| 17087 | 42BF
| 17088 | 42C0 | Export Active Energy | 0~9999 9999.9
| 17089 | 42C1
| 17090 | 42C2 | Total Reactive Energy | 0~9999 9999.9
| 17091 | 42C3
| 17092 | 42C4 | Import Reactive Energy | 0~9999 9999.9
| 17093 | 42C5
| 17094 | 42C6 | Export Reactive Energy | 0~9999 9999.9
| 17095 | 42C7
Last 7st month Energy (Flat-period Energy) | 17096 | 42C8 | Total Active Energy | 0~9999 9999.9
| 17097 | 42C9
| 17098 | 42CA | Import Active Energy | 0~9999 9999.9
| 17099 | 42CB
| 17100 | 42CC | Export Active Energy | 0~9999 9999.9
| 17101 | 42CD
| 17102 | 42CE | Total Reactive Energy | 0~9999 9999.9
| 17103 | 42CF
| 17104 | 42D0 | Import Reactive Energy | 0~9999 9999.9
| 17105 | 42D1
| 17106 | 42D2 | Export Reactive Energy | 0~9999 9999.9
| 17107 | 42D3
Last 7st month Energy (Valley-period Energy) | 17108 | 42D4 | Total Active Energy | 0~9999 9999.9
| 17109 | 42D5
| 17110 | 42D6 | Import Active Energy | 0~9999 9999.9
| 17111 | 42D7
| 17112 | 42D8 | Export Active Energy | 0~9999 9999.9
| 17113 | 42D9
| 17114 | 42DA | Total Reactive Energy | 0~9999 9999.9
| 17115 | 42DB
| 17116 | 42DC | Import Reactive Energy | 0~9999 9999.9
| 17117 | 42DD
| 17118 | 42DE | Export Reactive Energy | 0~9999 9999.9
| 17119 | 42DF
Last 8st month Energy (Total Energy) | 17120 | 42E0 | Total Active Energy | 0~9999 9999.9
| 17121 | 42E1
| 17122 | 42E2 | Import Active Energy | 0~9999 9999.9
| 17123 | 42E3
| 17124 | 42E4 | Export Active Energy | 0~9999 9999.9
| 17125 | 42E5
| 17126 | 42E6 | Total Reactive Energy | 0~9999 9999.9
| 17127 | 42E7
| 17128 | 42E8 | Import Reactive Energy | 0~9999 9999.9
| 17129 | 42E9
| 17130 | 42EA | Export Reactive Energy | 0~9999 9999.9
| 17131 | 42EB
Last 8st month Energy (Sharp-period Energy) | 17132 | 42EC | Total Active Energy | 0~9999 9999.9
| 17133 | 42ED
| 17134 | 42EE | Import Active Energy | 0~9999 9999.9
| 17135 | 42EF
| 17136 | 42F0 | Export Active Energy | 0~9999 9999.9
| 17137 | 42F1
| 17138 | 42F2 | Total Reactive Energy | 0~9999 9999.9
| 17139 | 42F3
| 17140 | 42F4 | Import Reactive Energy | 0~9999 9999.9
| 17141 | 42F5
| 17142 | 42F6 | Export Reactive Energy | 0~9999 9999.9
| 17143 | 42F7
Last 8st month Energy (Peak-period Energy) | 17144 | 42F8 | Total Active Energy | 0~9999 9999.9
| 17145 | 42F9
| 17146 | 42FA | Import Active Energy | 0~9999 9999.9
| 17147 | 42FB
| 17148 | 42FC | Export Active Energy | 0~9999 9999.9
| 17149 | 42FD
| 17150 | 42FE | Total Reactive Energy | 0~9999 9999.9
| 17151 | 42FF
| 17152 | 4300 | Import Reactive Energy | 0~9999 9999.9
| 17153 | 4301
| 17154 | 4302 | Export Reactive Energy | 0~9999 9999.9
| 17155 | 4303
Last 8st month Energy (Flat-period Energy) | 17156 | 4304 | Total Active Energy | 0~9999 9999.9
| 17157 | 4305
| 17158 | 4306 | Import Active Energy | 0~9999 9999.9
| 17159 | 4307
| 17160 | 4308 | Export Active Energy | 0~9999 9999.9
| 17161 | 4309
| 17162 | 430A | Total Reactive Energy | 0~9999 9999.9
| 17163 | 430B
| 17164 | 430C | Import Reactive Energy | 0~9999 9999.9
| 17165 | 430D
| 17166 | 430E | Export Reactive Energy | 0~9999 9999.9
| 17167 | 430F
Last 8st month Energy (Valley-period Energy) | 17168 | 4310 | Total Active Energy | 0~9999 9999.9
| 17169 | 4311
| 17170 | 4312 | Import Active Energy | 0~9999 9999.9
| 17171 | 4313
| 17172 | 4314 | Export Active Energy | 0~9999 9999.9
| 17173 | 4315
| 17174 | 4316 | Total Reactive Energy | 0~9999 9999.9
| 17175 | 4317
| 17176 | 4318 | Import Reactive Energy | 0~9999 9999.9
| 17177 | 4319
| 17178 | 431A | Export Reactive Energy | 0~9999 9999.9
| 17179 | 431B
Last 9st month Energy (Total Energy) | 17180 | 431C | Total Active Energy | 0~9999 9999.9
| 17181 | 431D
| 17182 | 431E | Import Active Energy | 0~9999 9999.9
| 17183 | 431F
| 17184 | 4320 | Export Active Energy | 0~9999 9999.9
| 17185 | 4321
| 17186 | 4322 | Total Reactive Energy | 0~9999 9999.9
| 17187 | 4323
| 17188 | 4324 | Import Reactive Energy | 0~9999 9999.9
| 17189 | 4325
| 17190 | 4326 | Export Reactive Energy | 0~9999 9999.9
| 17191 | 4327
Last 9st month Energy (Sharp-period Energy) | 17192 | 4328 | Total Active Energy | 0~9999 9999.9
| 17193 | 4329
| 17194 | 432A | Import Active Energy | 0~9999 9999.9
| 17195 | 432B
| 17196 | 432C | Export Active Energy | 0~9999 9999.9
| 17197 | 432D
| 17198 | 432E | Total Reactive Energy | 0~9999 9999.9
| 17199 | 432F
| 17200 | 4330 | Import Reactive Energy | 0~9999 9999.9
| 17201 | 4331
| 17202 | 4332 | Export Reactive Energy | 0~9999 9999.9
| 17203 | 4333
Last 9st month Energy (Peak-period Energy) | 17204 | 4334 | Total Active Energy | 0~9999 9999.9
| 17205 | 4335
| 17206 | 4336 | Import Active Energy | 0~9999 9999.9
| 17207 | 4337
| 17208 | 4338 | Export Active Energy | 0~9999 9999.9
| 17209 | 4339
| 17210 | 433A | Total Reactive Energy | 0~9999 9999.9
| 17211 | 433B
| 17212 | 433C | Import Reactive Energy | 0~9999 9999.9
| 17213 | 433D
| 17214 | 433E | Export Reactive Energy | 0~9999 9999.9
| 17215 | 433F
Last 9st month Energy (Flat-period Energy) | 17216 | 4340 | Total Active Energy | 0~9999 9999.9
| 17217 | 4341
| 17218 | 4342 | Import Active Energy | 0~9999 9999.9
| 17219 | 4343
| 17220 | 4344 | Export Active Energy | 0~9999 9999.9
| 17221 | 4345
| 17222 | 4346 | Total Reactive Energy | 0~9999 9999.9
| 17223 | 4347
| 17224 | 4348 | Import Reactive Energy | 0~9999 9999.9
| 17225 | 4349
| 17226 | 434A | Export Reactive Energy | 0~9999 9999.9
| 17227 | 434B
Last 9st month Energy (Valley-period Energy) | 17228 | 434C | Total Active Energy | 0~9999 9999.9
| 17229 | 434D
| 17230 | 434E | Import Active Energy | 0~9999 9999.9
| 17231 | 434F
| 17232 | 4350 | Export Active Energy | 0~9999 9999.9
| 17233 | 4351
| 17234 | 4352 | Total Reactive Energy | 0~9999 9999.9
| 17235 | 4353
| 17236 | 4354 | Import Reactive Energy | 0~9999 9999.9
| 17237 | 4355
| 17238 | 4356 | Export Reactive Energy | 0~9999 9999.9
| 17239 | 4357
Last 10st month Energy (Total Energy) | 17240 | 4358 | Total Active Energy | 0~9999 9999.9
| 17241 | 4359
| 17242 | 435A | Import Active Energy | 0~9999 9999.9
| 17243 | 435B
| 17244 | 435C | Export Active Energy | 0~9999 9999.9
| 17245 | 435D
| 17246 | 435E | Total Reactive Energy | 0~9999 9999.9
| 17247 | 435F
| 17248 | 4360 | Import Reactive Energy | 0~9999 9999.9
| 17249 | 4361
| 17250 | 4362 | Export Reactive Energy | 0~9999 9999.9
| 17251 | 4363
Last 10st month Energy (Sharp-period Energy) | 17252 | 4364 | Total Active Energy | 0~9999 9999.9
| 17253 | 4365
| 17254 | 4366 | Import Active Energy | 0~9999 9999.9
| 17255 | 4367
| 17256 | 4368 | Export Active Energy | 0~9999 9999.9
| 17257 | 4369
| 17258 | 436A | Total Reactive Energy | 0~9999 9999.9
| 17259 | 436B
| 17260 | 436C | Import Reactive Energy | 0~9999 9999.9
| 17261 | 436D
| 17262 | 436E | Export Reactive Energy | 0~9999 9999.9
| 17263 | 436F
Last 10st month Energy (Peak-period Energy) | 17264 | 4370 | Total Active Energy | 0~9999 9999.9
| 17265 | 4371
| 17266 | 4372 | Import Active Energy | 0~9999 9999.9
| 17267 | 4373
| 17268 | 4374 | Export Active Energy | 0~9999 9999.9
| 17269 | 4375
| 17270 | 4376 | Total Reactive Energy | 0~9999 9999.9
| 17271 | 4377
| 17272 | 4378 | Import Reactive Energy | 0~9999 9999.9
| 17273 | 4379
| 17274 | 437A | Export Reactive Energy | 0~9999 9999.9
| 17275 | 437B
Last 10st month Energy (Flat-period Energy) | 17276 | 435C | Total Active Energy | 0~9999 9999.9
| 17277 | 437D
| 17278 | 437E | Import Active Energy | 0~9999 9999.9
| 17279 | 437F
| 17280 | 4380 | Export Active Energy | 0~9999 9999.9
| 17281 | 4381
| 17282 | 4382 | Total Reactive Energy | 0~9999 9999.9
| 17283 | 4383
| 17284 | 4384 | Import Reactive Energy | 0~9999 9999.9
| 17285 | 4385
| 17286 | 4386 | Export Reactive Energy | 0~9999 9999.9
| 17287 | 4387
Last 10st month Energy (Valley-period Energy) | 17288 | 4388 | Total Active Energy | 0~9999 9999.9
| 17289 | 4389
| 17290 | 438A | Import Active Energy | 0~9999 9999.9
| 17291 | 438B
| 17292 | 438C | Export Active Energy | 0~9999 9999.9
| 17293 | 438D
| 17294 | 438E | Total Reactive Energy | 0~9999 9999.9
| 17295 | 438F
| 17296 | 4390 | Import Reactive Energy | 0~9999 9999.9
| 17297 | 4391
| 17298 | 4392 | Export Reactive Energy | 0~9999 9999.9
| 17299 | 4393
Last 11st month Energy (Total Energy) | 17300 | 4394 | Total Active Energy | 0~9999 9999.9
| 17301 | 4395
| 17302 | 4396 | Import Active Energy | 0~9999 9999.9
| 17303 | 4397
| 17304 | 4398 | Export Active Energy | 0~9999 9999.9
| 17305 | 4399
| 17306 | 439A | Total Reactive Energy | 0~9999 9999.9
| 17307 | 439B
| 17308 | 439C | Import Reactive Energy | 0~9999 9999.9
| 17309 | 439D
| 17310 | 439E | Export Reactive Energy | 0~9999 9999.9
| 17311 | 439F
Last 11st month Energy (Sharp-period Energy) | 17312 | 43A0 | Total Active Energy | 0~9999 9999.9
| 17313 | 43A1
| 17314 | 43A2 | Import Active Energy | 0~9999 9999.9
| 17315 | 43A3
| 17316 | 43A4 | Export Active Energy | 0~9999 9999.9
| 17317 | 43A5
| 17318 | 43A6 | Total Reactive Energy | 0~9999 9999.9
| 17319 | 43A7
| 17320 | 43A8 | Import Reactive Energy | 0~9999 9999.9
| 17321 | 43A9
| 17322 | 43AA | Export Reactive Energy | 0~9999 9999.9
| 17323 | 43AB
Last 11st month Energy (Peak-period Energy) | 17324 | 43AC | Total Active Energy | 0~9999 9999.9
| 17325 | 43AD
| 17326 | 43AE | Import Active Energy | 0~9999 9999.9
| 17327 | 43AF
| 17328 | 43B0 | Export Active Energy | 0~9999 9999.9
| 17329 | 43B1
| 17330 | 43B2 | Total Reactive Energy | 0~9999 9999.9
| 17331 | 43B3
| 17332 | 43B4 | Import Reactive Energy | 0~9999 9999.9
| 17333 | 43B5
| 17334 | 43B6 | Export Reactive Energy | 0~9999 9999.9
| 17335 | 43B7
Last 11st month Energy (Flat-period Energy) | 17336 | 43B8 | Total Active Energy | 0~9999 9999.9
| 17337 | 43B9
| 17338 | 43BA | Import Active Energy | 0~9999 9999.9
| 17339 | 43BB
| 17340 | 43BC | Export Active Energy | 0~9999 9999.9
| 17341 | 43BD
| 17342 | 43BE | Total Reactive Energy | 0~9999 9999.9
| 17343 | 43BF
| 17344 | 43C0 | Import Reactive Energy | 0~9999 9999.9
| 17345 | 43C1
| 17346 | 43C2 | Export Reactive Energy | 0~9999 9999.9
| 17347 | 43C3
Last 11st month Energy (Valley-period Energy) | 17348 | 43C4 | Total Active Energy | 0~9999 9999.9
| 17349 | 43C5
| 17350 | 43C6 | Import Active Energy | 0~9999 9999.9
| 17351 | 43C7
| 17352 | 43C8 | Export Active Energy | 0~9999 9999.9
| 17353 | 43C9
| 17354 | 43CA | Total Reactive Energy | 0~9999 9999.9
| 17355 | 43CB
| 17356 | 43CC | Import Reactive Energy | 0~9999 9999.9
| 17357 | 43CD
| 17358 | 43CE | Export Reactive Energy | 0~9999 9999.9
| 17359 | 43CF

## Demand
Maximum Demand
No, | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
1 | 16896 | 4200 | 03/04 | Maximum demand of the day | The day demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
2 | 16897 | 4201 | 03/04
3 | 16898 | 4202 | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
4 | 16899 | 4203 | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
5 | 16900 | 4204 | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
6 | 16901 | 4205 | 03/04 | Maximum demand of the last day | the last day demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
7 | 16902 | 4206 | 03/04
8 | 16903 | 4207 | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
9 | 16904 | 4208 | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
10 | 16905 | 4209 | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
11 | 16906 | 420A | 03/04 | Maximum demand of the month | The month demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
12 | 16907 | 420B | 03/04
13 | 16908 | 420C | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
14 | 16909 | 420D | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
15 | 16910 | 420E | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
16 | 16911 | 420F | 03/04 | Maximum demand of the last month | the last month demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
17 | 16912 | 4210 | 03/04
18 | 16913 | 4211 | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
19 | 16914 | 4212 | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
20 | 16915 | 4213 | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
21 | 16916 | 4214 | 03/04 | Phase A Circuit Maximum demand of the day | The day demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
22 | 16917 | 4215 | 03/04
23 | 16918 | 4216 | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
24 | 16919 | 4217 | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
25 | 16920 | 4218 | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
26 | 16921 | 4219 | 03/04 | Phase A Circuit Maximum demand of the last day | the last day demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
27 | 16922 | 421A | 03/04
28 | 16923 | 421B | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
29 | 16924 | 421C | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
30 | 16925 | 421D | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
31 | 16926 | 421E | 03/04 | Phase A Circuit Maximum demand of the month | The month demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
32 | 16927 | 421F | 03/04
33 | 16928 | 4220 | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
34 | 16929 | 4221 | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
35 | 16930 | 4222 | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
36 | 16931 | 4223 | 03/04 | Phase A Circuit Maximum demand of the last month | the last month demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
37 | 16932 | 4224 | 03/04
38 | 16933 | 4225 | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
39 | 16934 | 4226 | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
40 | 16935 | 4227 | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
41 | 16936 | 4228 | 03/04 | Phase B Circuit Maximum demand of the day | The day demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
42 | 16937 | 4229 | 03/04
43 | 16938 | 422A | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
44 | 16939 | 422B | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
45 | 16940 | 422C | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
46 | 16941 | 422D | 03/04 | Phase B Circuit Maximum demand of the last day | the last day demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
47 | 16942 | 422E | 03/04
48 | 16943 | 422F | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
49 | 16944 | 4230 | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
50 | 16945 | 4231 | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
51 | 16946 | 4232 | 03/04 | Phase B Circuit Maximum demand of the month | The month demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
52 | 16947 | 4233 | 03/04
53 | 16948 | 4234 | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
54 | 16949 | 4235 | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
55 | 16950 | 4236 | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
56 | 16951 | 4237 | 03/04 | Phase B Circuit Maximum demand of the last month | the last month demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
57 | 16952 | 4238 | 03/04
58 | 16953 | 4239 | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
59 | 16954 | 423A | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
60 | 16955 | 423B | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
61 | 16956 | 423C | 03/04 | Phase C Circuit Maximum demand of the day | The day demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
62 | 16957 | 423D | 03/04
63 | 16958 | 423E | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
64 | 16959 | 423F | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
65 | 16960 | 4240 | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
66 | 16961 | 4241 | 03/04 | Phase C Circuit Maximum demand of the last day | the last day demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
67 | 16962 | 4242 | 03/04
68 | 16963 | 4243 | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
69 | 16964 | 4244 | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
70 | 16965 | 4245 | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
71 | 16966 | 4246 | 03/04 | Phase C Circuit Maximum demand of the month | The month demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
72 | 16967 | 4247 | 03/04
73 | 16968 | 4248 | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
74 | 16969 | 4249 | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
75 | 16970 | 424A | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535
76 | 16971 | 424B | 03/04 | Phase C Circuit Maximum demand of the last month | the last month demand | Unsigned 32-bit | 0 | 0-4294967295 | kW
77 | 16972 | 424C | 03/04
78 | 16973 | 424D | 03/04 |  | Time:Year, second | Unsigned 16-bit | 0 | 0-65535
79 | 16974 | 424E | 03/04 |  | Time:Month Day | Unsigned 16-bit | 0 | 0-65535
80 | 16975 | 424F | 03/04 |  | Time:Hour Minute | Unsigned 16-bit | 0 | 0-65535

## DI
DI（Function Code 02, read）
No, | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Default | Value Range
1 | 0 | 0000 | 02 Read | Digital Input (ONLY Read) | DI1 | 0 | 0~1
2 | 1 | 0001 |  |  | DI2 | 0 | 0~1
0: open;1: closed）

## Fault Parameter
Fault Parameter Setting
No, | Address (Decimal) | Address (Hexadecimal) | Function Code (Hexadecimal) | Parameter |  | Data Type | Default Value | Value Range | Unit | Remark
3 | 9795 | 2643 | 03 Read 06/10 Write | Lack Phase A | Shield fault setting | Unsigned 16-bit | 0 | 0一1 | —— | 0: no shielded， 1：shielded
4 | 9796 | 2644 | 03 Read 06/10 Write |  | Setting Value | Unsigned 16-bit | 120 | 0一65535 | ——
5 | 9797 | 2645 | 03 Read 06/10 Write |  | Fault delay time | Unsigned 32-bit | 400 | 0一65535000 | mS
6 | 9798 | 2646 | 03 Read 06/10 Write
7 | 9799 | 2647 | 03 Read 06/10 Write |  | Recory Value Setting | Unsigned 16-bit | 118 | 0一65535 | ——
8 | 9800 | 2648 | 03 Read 06/10 Write |  | Recovery fault delay time | Unsigned 32-bit | 1000 | 0一65535000 | mS
9 | 9801 | 2649 | 03 Read 06/10 Write
14 | 9806 | 264E | 03 Read 06/10 Write | Lack Phase B | Reserved | Unsigned 16-bit | 0 | 0 | ——
15 | 9807 | 264F | 03 Read 06/10 Write |  | Reserved | Unsigned 16-bit | 0 | 0 | ——
16 | 9808 | 2650 | 03 Read 06/10 Write |  | Shield fault setting | Unsigned 16-bit | 0 | 0一1 | —— | 0: no shielded， 1：shielded
17 | 9809 | 2651 | 03 Read 06/10 Write |  | Setting Value | Unsigned 16-bit | 120 | 0一65535 | ——
18 | 9810 | 2652 | 03 Read 06/10 Write |  | Fault delay time | Unsigned 32-bit | 400 | 0一65535000 | mS
19 | 9811 | 2653 | 03 Read 06/10 Write
20 | 9812 | 2654 | 03 Read 06/10 Write |  | Recory Value Setting | Unsigned 16-bit | 118 | 0一65535 | ——
21 | 9813 | 2655 | 03 Read 06/10 Write |  | Recovery fault delay time | Unsigned 32-bit | 1000 | 0一65535000 | mS
22 | 9814 | 2656 | 03 Read 06/10 Write
27 | 9819 | 265B | 03 Read 06/10 Write | Lack Phase C | Reserved | Unsigned 16-bit | 0 | 0 | ——
28 | 9820 | 265C | 03 Read 06/10 Write |  | Reserved | Unsigned 16-bit | 0 | 0 | ——
29 | 9821 | 265D | 03 Read 06/10 Write |  | Shield fault setting | Unsigned 16-bit | 0 | 0一1 | —— | 0: no shielded， 1：shielded
30 | 9822 | 265E | 03 Read 06/10 Write |  | Setting Value | Unsigned 16-bit | 120 | 0一65535 | ——
31 | 9823 | 265F | 03 Read 06/10 Write |  | Fault delay time | Unsigned 32-bit | 400 | 0一65535000 | mS
32 | 9824 | 2660 | 03 Read 06/10 Write
33 | 9825 | 2661 | 03 Read 06/10 Write |  | Recory Value Setting | Unsigned 16-bit | 118 | 0一65535 | ——
34 | 9826 | 2662 | 03 Read 06/10 Write |  | Recovery fault delay time | Unsigned 32-bit | 1000 | 0一65535000 | mS
35 | 9827 | 2663 | 03 Read 06/10 Write
40 | 9832 | 2668 | 03 Read 06/10 Write | phase sequence fault | Reserved | Unsigned 16-bit | 0 | 0 | ——
41 | 9833 | 2669 | 03 Read 06/10 Write |  | Reserved | Unsigned 16-bit | 0 | 0 | ——
42 | 9834 | 266A | 03 Read 06/10 Write |  | Shield fault setting | Unsigned 16-bit | 0 | 0一1 | —— | 0: no shielded， 1：shielded
43 | 9835 | 266B | 03 Read 06/10 Write |  | Setting Value | Unsigned 16-bit | 120 | 0一65535 | ——
44 | 9836 | 266C | 03 Read 06/10 Write |  | Fault delay time | Unsigned 32-bit | 400 | 0一65535000 | mS
45 | 9837 | 266D | 03 Read 06/10 Write
46 | 9838 | 266E | 03 Read 06/10 Write |  | Recory Value Setting | Unsigned 16-bit | 118 | 0一65535 | ——
47 | 9839 | 266F | 03 Read 06/10 Write |  | Recovery fault delay time | Unsigned 32-bit | 1000 | 0一65535000 | mS
48 | 9840 | 2670 | 03 Read 06/10 Write